## Generating Stations
Station_Name | GroupName | Owner_Name | Operators_Name | Connection_Type | Generation_Type | Operating_Capacity | Fuel_Name | Primary_Efficiency | Secondary_Fuel | Secondary_Efficiency | Date_Commissioned | Year | Installed_Capacity | Max_Unit_Size | Typical_Annual_GWh | Generating_Units | Thermal_Operating_Stockpile | Hydro_Max_m3_Storage | Hydro_Max_GWh_Storage | Node_Name | Region_Name | Island_Name | Comments | Decommission_Date | Data_Source | GroupOrder | CDSName | POC analysis
Addington |  | Orion | Meridian Energy | Embedded | Unknown | 0.4 | Unknown | 0 | Not Applicable | 0 |  |  | 0.4 | 0.4 MW | 0 |  |  | 0 |  | ADD0111 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Christchurch.Addington.Rail | 0
Aluminium Diecasting Ltd |  | Aluminium Diecasting | Meridian Energy | Embedded | Unknown | 0.2 | Unknown | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0 |  |  | 0 |  | BRY0111 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Christchurch.Bromley.Diecast | 0
Amethyst |  | Westpower | Westpower | Embedded | Hydro | 6 | Hydro | 0 | Not Applicable | 0 | Jun 2013 | 2013 | 6 | 6 MW | 30 |  |  | 0 |  | ARA2201 | WEC - West Coast | SI - South Island | GWh estimated |  | www.energynews.co.nz |  | No current series | #N/A
Anchor Products |  | Trustpower | Trustpower | Embedded | Thermal | 3.9 | Unknown | 0 | Not Applicable | 0 |  |  | 3.9 | 3.9 MW | 3.3 |  |  | 0 |  | TMU0111 | WTO - Waikato | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.TeAwamutu | 0
Aniwhenua |  | Bay of Plenty Energy | Todd Energy | Partially Embedded | Hydro | 25 | Hydro | 0.173 | Not Applicable | 0 | 1979 | 1979 | 25 | 12.5 MW | 105 | 2 x 12.5 MW |  | 0 |  | MAT1101 | BOP - Bay Of Plenty | NI - North Island | Constructed over three years at a cost of $27 million in the late 1970's, the Aniwhenua scheme involved the damming of the Rangitaiki River, forming a 255 hectare storage lake. Aniwhenua is named after the falls which are adjacent to the power house. The Aniwhenua scheme consists of a 200 meter long, 10 meter high dam structure with two radial control gates which can discharge 1,270 cubic meters of water per second. Three additional flap gates are designed to handle higher flood conditions. A 2.2 kilometer canal with a fall rate of 1 in 2,500 diverts water from the lake to a head pond above the powerhouse. Water flows from the head of the pond through steeply dropping penstocks at a rate of 75 cubic meters a second to the powerhouse. There, it drives two 12.5 MW generators before being discharged back to the river just below the Aniwhenua Falls. |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Aniwhenua | 0
Arapuni | Waikato Hydro Scheme | Mighty River Power | Mighty River Power | Grid Connected | Hydro | 196.7 | Hydro | 0.463 | Not Applicable | 0 | Oct 1946 | 1946 | 196.7 | 26.7 MW | 805 |  |  | 10 |  | ARI1101 | WTO - Waikato | NI - North Island | With eight generating units, Arapuni has the largest single capacity of any of the stations in the Waikato hydro system. Due to its close proximity to Hamilton's urban centre, Arapuni provides a voltage support role for power transmissions to the area. Recent upgrades to the station have enhanced its capability in this area. This station is occasionally used for frequency keeping. The Arapuni power station was the first government-built hydroelectric station on the Waikato River. During the initial surveying in 1916, an old watercourse was found just upstream of one of the narrowest parts of the gorge. In 1920, the surveying was halted due to lack of government funds to progress the project. Construction finally began in 1924, but repeated heavy rain and the resulting floods dogged the early works. Just after the project was commissioned in mid-1929, the station was closed for two years while a water seepage problem was investigated and the headrace lined. The station began operating again in May 1932 with four generators installed. Four more machines have since been added. In 2001, work was completed on four of Arapuni's turbines to increase capacity from 24.7MW to 26.7MW each and to improve their peak efficiency to 94 percent. |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List), www.mightyriverpower.co.nz | 7 | GEN.Hydro.Waikato.Arapuni | 0
Aratiatia | Waikato Hydro Scheme | Mighty River Power | Mighty River Power | Grid Connected | Hydro | 78 | Hydro | 0.268 | Not Applicable | 0 | May 1964 | 1964 | 90 | 30 MW | 330 |  |  | 0 |  | ARA2201 | WTO - Waikato | NI - North Island | As the smallest of the hydro reservoirs, Aratiatia's lake level fluctuates through its storage range regularly throughout the day. Aratiatia is largely a 'run of river' station, passing water released from the Taupo Gates down to Lake Ohakuri. |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List) | 1 | GEN.Hydro.Waikato.Aratiatia | 0
Argyle | Branch Hydro Scheme | Trustpower | Trustpower | Grid Connected | Hydro | 3.8 | Hydro | 0 | Not Applicable | 0 | May 1983 | 1983 | 3.8 | 3.8 MW | 17 |  |  | 0 |  | ARG1101 | NEL - Nelson/Marlbourough | SI - South Island | Investigations into the feasibility of Branch River Power scheme began in 1978, and following a detailed investigation in 1980 finance was approved with construction beginning soon afterwards. Canal filling commenced in March 1983, with generation commencing at the Wairau Power House in June, and at Argyle two months later.A run of the river scheme with daily storage, the water first passes through the Argyle station of 3800kw capacity with a head of 21.9 meters. A 3385 meter canal then carries the water to the Wairau Power Station of 7200kw at a head of 41.3 metres. CDS output data is believed to be net of some local load. |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) | 1 | SI.Argyle.Import | 0
Arnold |  | Trustpower | Trustpower | Embedded | Hydro | 3.1 | Hydro | 0 | Not Applicable | 0 | 1932 | 1932 | 3.1 | 3.1 MW | 20 |  |  | 0 |  | DOB0331 | WEC - West Coast | SI - South Island | Estimated GWH based on high capacity usage |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Arnold | 0
Ascot Ave |  | Manson Developments | Mighty River Power | Embedded | Unknown | 0.1 | Unknown | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0 |  |  | 0 |  | PEN0331 | AKL - Auckland | NI - North Island |  |  | EMS (Reconciliation Manager List),CDS |  | GEN.Unknown.Auckland.Mansons.Penrose | 0
Atiamuri | Waikato Hydro Scheme | Mighty River Power | Mighty River Power | Grid Connected | Hydro | 84 | Hydro | 0.204 | Not Applicable | 0 | Apr 1962 | 1962 | 84 | 21 MW | 289 |  |  | 0 |  | ATI2201 | BOP - Bay Of Plenty | NI - North Island | Construction was completed six months ahead of schedule and the station was commissioned early in November 1958. The additional generation from the Atiamuri station, together with the newly built Meremere coal-fired station, allowed post-war electricity restrictions in the North Island to be lifted by Christmas 1958. Although originally designed for three generators, a fourth was later added and commissioned in 1962. (Note : The reconcilation process models Atiamuri as a grid connected network rather than generation) |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List) | 3 | GEN.Hydro.Waikato.Atiamuri | 0
Auckland District Hospital |  | Auckland District Hospital Board | Meridian Energy | Embedded | Cogeneration | 3.6 | Gas | 0 | Diesel | 0 | Apr 2005 | 2005 | 3.6 | 1.8 MW | 7 | 2 x 1.8MW |  | 0 |  | PEN0331 | AKL - Auckland | NI - North Island | Built by Energy for Industry, Baseload heat: 4.2MW, electricity: 3.6MW net, standby power: 2.8MW |  | www.meridianenergy.co.nz,EL Database,EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Auckland.Hospital | 0
Aviemore | Waitaki Hydro Scheme | Meridian Energy | Meridian Energy | Grid Connected | Hydro | 220 | Hydro | 0.31 | Not Applicable | 0 | 1968 | 1968 | 220 | 55 MW | 930 |  |  | 17 |  | AVI2201 | SCN - South Canterbury | SI - South Island | Due to limited storage capacity Aviemore predominantly acts as run of river station with as water flows from Lake Benmore and through to Lake Waitaki. |  | www.meridianenergy.co.nz,Electricity Commission,EMS (Reconciliation Manager List) | 7 | GEN.Hydro.Waitaki.Aviemore | 0
Ballance Agri |  | Trustpower | Trustpower | Embedded | Cogeneration | 6.5 | Unknown | 0 | Not Applicable | 0 |  |  | 6.5 | 6.5 MW | 11 |  |  | 0 |  | MTM0111 | BOP - Bay Of Plenty | NI - North Island |  |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.MountMaunganui | 0
Bay Milk Edgecumbe |  | Bay of Plenty Energy | Todd Energy | Embedded | Cogeneration | 10 | Gas | 12500 | Not Applicable | 0 | 1996 | 1996 | 10 | 5 MW | 54 | 2 x 5 MW |  | 0 |  | EDG0331 | BOP - Bay Of Plenty | NI - North Island |  |  | PB 'Thermal & Geothermal Generation Capabilities',EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.Edgecumbe | 0
Belfast |  | Christchurch City Council | Meridian Energy | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | PAP0111 | CAN - Canterbury | SI - South Island |  |  | EMS (Reconciliation Manager List) |  | GEN.Unknown.Christchurch.Papanui.Belfast | 0
Benmore | Waitaki Hydro Scheme | Meridian Energy | Meridian Energy | Grid Connected | Hydro | 540 | Hydro | 0.818 | Not Applicable | 0 | 1965 | 1965 | 540 | 94 MW | 2500 |  |  | 74 |  | BEN2202 | SCN - South Canterbury | SI - South Island | Lake Benmore draws water from the Ohau, Pukaki and Tekapo Rivers and the Ohau canal as the culmination point for the outflows from the Upper Waitaki stations. With a capacity of 540 MW the Benmore station is the largest of the Waitaki system. Benmore is also the location of the southern stating point of the HVDC line that links the electricity systems of the North and South Islands. Previously injected onto the grid through 2 metered buses BEN0162 and BEN0163. Since reconfigured and injects through BEN2202. |  | www.meridianenergy.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) | 6 | GEN.Hydro.Waitaki.Benmore | 0
Blue Mountain Lumber |  | Blue Mountain Lumber | Meridian Energy | Embedded | Cogeneration | 1.4 | Wood_waste | 0 | Not Applicable | 0 | 2000 | 2000 | 1.4 | 1.4 MW | 1.9 |  |  | 0 |  | GOR0331 | OTG - Otago/Southland | SI - South Island | There is a 10 MWth steam boiler fuelled by the sawmill wood residues and a 1.4 MWe steam turbine generator to utilise any surplus steam for electricity generation. The 1.9 Gwh annual output reflects the turbine being used as a means to dump heat and so is operated for about 20% of the time. |  | EMS (Reconciliation Manager List),www.bioenergy.org.nz |  | GEN.Thermal.Gore | 0
Bombay |  | Greymouth Power Company | Contact Energy | Embedded | Unknown | 2.3 | Unknown | 0 | Not Applicable | 0 |  |  | 2.3 | 2.3 MW | 0 |  |  | 0 |  | BOB1101 | AKL - Auckland | NI - North Island | GWh and MW estimated from Centralised Dataset |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Auckland.Bombay | 0
Brooklyn Power Station |  | Lloyd Wensley | Lloyd Wensley | Embedded | Hydro | 0.2 | Hydro | 0 | Not Applicable | 0 | 1934 | 1934 | 0.2 | 0.2 MW | 1 |  |  | 0 |  | MOT0111 | NEL - Nelson/Marlbourough | SI - South Island |  |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List),www.networktasman.co.nz, CDS |  | GEN.Hydro.Motueka.Brooklyn | 0
Burwood Hospital |  | Christchurch District Health | Meridian Energy | Embedded | Unknown | 0.2 | Unknown | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0 |  |  | 0 |  | BRY0661 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Christchurch.Bromley.Hospital | 0
Chathams Wind |  | CBD Energy | CBDEnergy | Embedded | Wind | 0.45 | Wind | 0 | Not Applicable | 0 | 2010 | 2010 | 0.45 | 0.225 MW | 1.4 | 2 x 0.225 MW |  | 0 |  | OFFGRID | OTH - Other | OT - Other | The wind farm has two 225kW Vergnet machines, which have been integrated with the existing diesel generation plant on the island. The turbines are two-bladed machines designed in France. They are designed so they can be raised and lowered on guy ropes, mainly to prevent damage during storms, but also for maintenance. |  | windenergy.org.nz |  | No current series | 0
Christchurch Airport (Harewood) |  | Christchurch Airport Authority | Meridian Energy | Embedded | Backup generation | 0.1 | Unknown | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0 |  |  | 0 |  | ISL0661 | CAN - Canterbury | SI - South Island | 818 Wairakai Road, Harewood. '3 units (separate points of supply) HAR0011 HAR0012 HAR0013. Max generation 0.04MW for HAR0011, 0.09MW for HAR0012 and 0.11 MW for HAR0013 |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Christchurch.Islington.Airport.1,GEN.Thermal.Christchurch.Islington.Airport.2,GEN.Thermal.Christchurch.Islington.Airport.3 | 0
Christchurch City Wastewater |  | Orion | Meridian Energy | Embedded | Other | 3.2 | Biogas | 0 | Not Applicable | 0 | Jan 1996 | 1996 | 3.2 | 3.2 MW | 2 |  |  | 0 |  | BRY0111 | CAN - Canterbury | SI - South Island |  |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List),CDS |  | GEN.Thermal.Christchurch.Bromley.Sewage | 0
Christchurch Hospital Campus |  | Christchurch District Health | Meridian Energy | Embedded | Backup generation | 0.3 | Unknown | 0 | Not Applicable | 0 |  |  | 0.3 | 0.3 MW | 0 |  |  | 0 |  | ADD0661 | CAN - Canterbury | SI - South Island | Backup plant, max generation in CDS 0.26 MW |  | EMS (Reconciliation Manager List),CDS |  | GEN.Unknown.Christchurch.Addington.Hospital | 0
Christchurch Wind Turbine |  | Orion | Meridian Energy | Embedded | Wind | 0.5 | Wind | 0 | Not Applicable | 0 | 2003 | 2003 | 0.5 | 0.5 MW | 0.8 |  |  | 0 |  | SPN0331 | CAN - Canterbury | SI - South Island | Located at Gebbies Pass. GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Wind.Christchurch.Springston | 0
Cleardale |  | MainPower | MainPower | Embedded | Hydro | 0.9 | Hydro | 0 | Not Applicable | 0 | 2010 | 2010 | 0.9 | 0.9 MW | 4 |  |  | 0 |  | ASB0661 | CAN - Canterbury | SI - South Island |  |  | EnergyNews |  | No current series | 0
Cloudy Bay |  | Indevin | Trustpower | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island |  |  | EMS (Reconciliation Manager List),CDS |  | GEN.Unknown.Blenheim.CloudyBay | 0
Clyde | Clutha Hydro Scheme | Contact Energy | Contact Energy | Grid Connected | Hydro | 432 | Hydro | 0.513 | Not Applicable | 0 | 1992 | 1992 | 432 | 108 MW | 2050 | 4 x 108 MW |  | 24 |  | CYD2201 | OTG - Otago/Southland | SI - South Island | Clyde is the largest concrete gravity dam in New Zealand. There are a million cubic metres of concrete in the dam with another 200,000 cubic metres in the powerhouse. Before Lake Dunstan could be filled and the power station commissioned, a great deal of landslide stabilisation work was carried out behind the dam. Over 14 kilometres of tunnels were excavated into the hillsides to prevent water build-up that could destabilise the hillsides. Huge buttresses of compacted rock and gravel have been built to strengthen the hillsides and a total of 3,500 measuring and monitoring instruments have been installed around the lakeshore. |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Clutha.Clyde | 0
Cobb |  | Trustpower | Trustpower | Grid Connected | Hydro | 32 | Hydro | 4.405 | Not Applicable | 0 | 1956 | 1956 | 34.3 | 10.45 MW | 190 | 4 x 3.35 MW, 2 x 10.45 MW |  | 24 |  | COB0661 | NEL - Nelson/Marlbourough | SI - South Island | Cobb is located in the Tasman Mountains northwest of Nelson, at the confluence of the Cobb and Takaka Rivers. The Cobb station was built by the Government during the 1940s and 1950s and connected to the national grid in 1956. The station was put up for sale in 1999 following the carve-up of state-owned ECNZ into three companies - Meridian Energy, Mighty River Power and Genesis. NGC acquired the Cobb Valley station in 2000, when it bought TransAlta New Zealand. TransAlta had owned the station for just over a year, after buying it from Meridian Energy. In March 2003 TrustPower completed the purchase of the Cobb hydro power station for $92.5m from NGC. |  | www.trustpower.co.nz,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Cobb | 0
Coleridge |  | Trustpower | Trustpower | Grid Connected | Hydro | 45 | Hydro | 1.009 | Not Applicable | 0 | 1914 | 1914 | 45 | 9.5 MW | 300 |  |  | 138 |  | COL0661 | CAN - Canterbury | SI - South Island | The Coleridge power station, about 100km inland from Christchurch, was New Zealand's first major hydropower scheme. The Government completed a study of the suitability of the area for hydro electricity generation in 1906 and commenced work in 1911. In 1914 the power station was commissioned with three turbines and was then progressively expanded over the next decade. Much of the station still dates from this period. In 1930 the Acheron River was diverted into Lake Coleridge, increasing the catchment area to more than 800 square kilometres and in 1977 a diversion of the Wilberforce River further increased the amount of water, boosting average annual output to 205 GWh. The Coleridge power station is fed from Lake Coleridge via 2 kilometres of tunnels and pipes, and after passing through the powerhouse the water empties into the Rakaia River approximately 140 meters below the level of the Lake. Lake Coleridge can store 2 to 3 months inflows. TrustPower purchased Coleridge from ECNZ in October 1998 for $91 million and over the next two years upgraded the station at a cost of about $6 million. The investment increased capacity from 36 MW to 45 MW and target annual output from 205 GWh to 300 GWh. Resource consents to re-permit the existing scheme were granted in 1996 for a 35-year term to 2031. |  | www.trustpower.co.nz, EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Coleridge | 0
Crowne Plaza |  | Crowne Plaza | Meridian Energy | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0 |  |  | 0 |  | ADD0661 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year. Assumed decommissioned with the demolition of the earthquake damaged Crown Plaza building. | 2011 | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Christchurch.Addington.CrownePlaza | 0
Darfield |  | WD Boyes & Sons | Meridian Energy | Embedded | Thermal | 0.1 | Diesel | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0 |  |  | 0 |  | HOR0331 | CAN - Canterbury | SI - South Island | Canterbury Clay Bricks, Negligible GWh |  | EMS (Reconciliation Manager List) |  | GEN.Thermal.Darfield | 0
Deep Stream |  | Trustpower | Trustpower | Embedded | Hydro | 5 | Hydro | 0 | Not Applicable | 0 | Dec 2008 | 2008 | 5 | 2.5 MW | 25 |  |  | 0 |  | HWB0331 | OTG - Otago/Southland | SI - South Island |  |  | www.trustpower.co.nz |  | No current series | 0
Dillmans | Dillmans Hydro Power Scheme | Trustpower | Trustpower | Embedded | Hydro | 3.5 | Hydro | 0 | Not Applicable | 0 | 1928 | 1928 | 3.5 | 3.5 MW | 16 |  |  | 0 |  | KUM0661 | WEC - West Coast | SI - South Island | This scheme had its beginnings in 1927, with power being generated for the first time in 1928. The scheme today consists of the Duffers Power Station, fed by races that in turn feed into the Kawhaka Creek, downstream artificial lake storage that in turn feeds the Dillmans Power Station, and the Kumara Power station fed by a race from Dillmans. With heads of 13 metres at Duffers, 46 metres at Dillmans and 78 metres at Kumara, and capacities of 500 kW, 3,500 kW and 6,500 kW respectively, the scheme has an average annual output of 47.9 GWh. |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Kumara.Dillmans | 0
Drysdale |  | Drysale Hydro Company | Mighty River Power | Embedded | Hydro | 0.1 | Hydro | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0.3 |  |  | 0 |  | MTN0331 | CEN - Central | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Drysdale | 0
Duffers | Dillmans Hydro Power Scheme | Trustpower | Trustpower | Embedded | Hydro | 0.5 | Hydro | 0 | Not Applicable | 0 | 1928 | 1928 | 0.5 | 0.5 MW | 2 |  |  | 0 |  | KUM0662 | WEC - West Coast | SI - South Island | This scheme had its beginnings in 1927, with power being generated for the first time in 1928. The scheme today consists of the Duffers Power Station, fed by races that in turn feed into the Kawhaka Creek, downstream artificial lake storage that in turn feeds the Dillmans Power Station, and the Kumara Power station fed by a race from Dillmans. With heads of 13 metres at Duffers, 46 metres at Dillmans and 78 metres at Kumara, and capacities of 500 kW, 3,500 kW and 6,500 kW respectively, the scheme has an average annual output of 47.9 GWh. |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Kumara.Duffers | 0
Enfield |  | Network Waitaki | Meridian Energy | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | OAM0331 | OTG - Otago/Southland | SI - South Island |  |  | EMS (Reconciliation Manager List) |  | GEN.Unknown.Enfield | 0
Esk |  | Trustpower | Trustpower | Embedded | Hydro | 4 | Hydro | 0 | Not Applicable | 0 | 2013 | 2013 | 4.2 | 2.8 MW | 15 |  |  | 0 |  | RDF0331 | HBY - Hawkes Bay | NI - North Island | The Esk scheme consists of two power stations situated on the Esk river in Hawkes Bay. Rimu Power Station has a head of 140 m and uses a maximum flow of one cubic metre a second (m3/s) of water to produce up to 1.4 MW of power. Toronui Power Station has a head of 320 m and uses no more than 1.2 m3/s to produce up to 2.8 MW. While Toronui has a head pond that can store about 4000 cubic metres the scheme is essentially run-of-river. |  | www.trustpower.co.nz |  | No current series | #N/A
Falls Dam |  | Pioneer Generation | Trustpower | Embedded | Hydro | 1.3 | Hydro | 0 | Not Applicable | 0 |  |  | 1.3 | 1.3 MW | 9 |  |  | 0 |  | NSY0331 | OTG - Otago/Southland | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.FallsDam | 0
Flat Hill |  | Pioneer Generation | Trustpower | Embedded | Wind | 6.8 | Wind | 0 | Not Applicable | 0 | Aug 2015 | 2015 | 6.8 | 0.85 MW | 24 | 8 x 0.85 MW |  | 0 |  | INV0331 | OTG - Otago/Southland | SI - South Island | Annual output estimated based on 40% utilisation |  | www.windenergy.org.nz/flat-hill |  | No current series | #N/A
Fletcher Forests |  | Trustpower | Trustpower | Embedded | Thermal | 3.5 | Wood_waste | 0 | Not Applicable | 0 |  |  | 3.5 | 3.5 MW | 26 |  |  | 0 |  | ROT0111 | BOP - Bay Of Plenty | NI - North Island | GWh data from Centralised Dataset 2006 calendar year, capacity 3.5MW, average closer to 3MW |  | EMS (Reconciliation Manager List), CDS, Fletcher Forests |  | GEN.Thermal.Rotorua.Waipa | 0
FoodStuffs Hickory Place |  | Foodstuffs (South Island) | Meridian Energy | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | ISL0331 | CAN - Canterbury | SI - South Island | GWh and MW estimated from Centralised Dataset |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Christchurch.Islington.Foodstuffs | 0
Forest Research |  | Todd Energy | Todd Energy | Embedded | Thermal | 0.3 | Gas | 0 | Not Applicable | 0 |  |  | 0.3 | 0.3 MW | 0 |  |  | 0 |  | ROT0111 | BOP - Bay Of Plenty | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Rotorua.ForestResearch | 0
Fox |  | Trustpower | Trustpower | Embedded | Hydro | 0.2 | Hydro | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 1.9 |  |  | 0 |  | HKK0661 | WEC - West Coast | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Fox.11KV | 0
Fraser |  | Pioneer Generation | Trustpower | Embedded | Hydro | 2.8 | Hydro | 0 | Not Applicable | 0 | 1956 | 1956 | 2.8 | 2.8 MW | 19 |  |  | 0 |  | CYD0331 | OTG - Otago/Southland | SI - South Island |  |  | Electricity Commission,EMS (Reconciliation Manager List),www.codc.govt.nz |  | GEN.Hydro.Fraser | 0
Gisborne |  | Eastland Networks | Contact Energy | Embedded | Unknown | 4 | Unknown | 0 | Not Applicable | 0 |  |  | 4.5 | 4.5 MW | 1.2 |  |  | 0 |  | GIS0501 | HBY - Hawkes Bay | NI - North Island | GWh from Centralised Dataset 2006 calendar year. CDS peak was 21.1MW but only occurred once in 2006, ramping up and down over a 3 hour period and again to a peak of 12.5MW 2 days later (origin unknown). Normal generation appears to peak at around 4.5MW |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Gisborne | 0
Glenbrook |  | Alinta Energy | Alinta Energy | Grid Connected Cogen | Cogeneration | 112 | Gas | 0 | Not Applicable | 0 | 1997 | 1997 | 112 | 74 MW | 550 |  |  | 0 |  | GLN0332 | AKL - Auckland | NI - North Island | Glenbrook Cogeneration Plant produces electricity using the by-product gasses from BHP Steel's New Zealand Steel's direct reduction iron-making process. The facility generates about 550,000 megawatt hours a year of electricity. Heating raw materials as part of the iron production process creates gases. The gases are used to fuel boilers which provide steam for turbines to generate electricity at two stages in the iron-making process: from four multiple hearth furnaces, which heat iron sand and coal; and at four direct reduction rotary kilns, which reduce the heated sand and coal char to a metalised product. Together with the multiple hearth furnace cogeneration plant, Glenbrook Cogeneration Plant produces around half of the steel mill's annual power requirements. Glenbrook generates at 11kv and 33kv (GLN0111 and GLN0332). Continuous output rating for the 38MW unit is around 25MW |  | EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List), ACS Data |  | GEN.Thermal.Glenbrook.SteelMill.Furnace,GEN.Thermal.Glenbrook.SteelMill.Kiln, GEN.Thermal.Glenbrook.Diesel | GLN0332 GLN0
Government Communications Satellite |  | Government Communications Satellite | Trustpower | Embedded | Backup generation | 0 | Diesel | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island |  |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Waihopai | 0
Greenmount Landfill |  | EnviroWaste | Mighty River Power | Embedded | Other | 5.5 | Biogas | 0 | Not Applicable | 0 | Feb 1992 | 1992 | 5.5 | 0.92 MW | 38 | 6 x 0.92 MW |  | 0 |  | OTA0221 | AKL - Auckland | NI - North Island | Annual output of 38GWh has been estimated based on 80% utilisation. Meter data series GMT0221 MRPL EG, reconciliation manager series GMT0221 VECT EG. The landfill has closed to new refuse. Gas extraction may continue for 10-20 years after landfill closure. |  | PB 'Thermal & Geothermal Generation Capabilities',EMS (Reconciliation Manager List),www.entec.co.nz |  | GEN.Thermal.Auckland.Greenmount | 0
Hampton Downs Landfill |  | EnviroWaste | Mighty River Power | Embedded | Other | 4 | Biogas | 0 | Not Applicable | 0 | 2009 | 2009 | 4 | 1 MW | 28 | 4 x 1 MW |  | 0 |  | MER0331 | WTO - Waikato | NI - North Island | Annual output of 28GWh has been estimated based on 80% utilisation |  | www.envirowaste.co.nz, |  | No current series | 0
Hau Nui |  | Genesis Energy | Genesis Energy | Embedded | Wind | 8.45 | Wind | 0 | Not Applicable | 0 | 1996 | 1996 | 8.45 | 0.6 MW | 22 | 15 x 0.6 MW |  | 0 |  | GYT0331 | WEL - Wellington | NI - North Island | Hau Nui wind farm is situated about 20 kilometres from the Martinborough township. Stage 1 commissioned in 1996 with 3.65 MW capacity, stage 2 commissioned in Dec 2004 with 4.8 MW The structures are designed to withstand wind speeds up to 240km/h. The 15 turbines operate in a wind speed range of 10 - 120 km/h above which they shut down. |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Wind.HauNui | 0
Highbank | Rangitata Diversion Race | Trustpower | Trustpower | Partially Embedded | Hydro | 25.2 | Hydro | 0 | Not Applicable | 0 | 1945 | 1945 | 25.2 | 25.2 MW | 94 |  |  | 0 |  | ASB0661 | CAN - Canterbury | SI - South Island | The Highbank Power Station was constructed between 1939 and 1945 as part of a combined project to irrigate dry farmland and generate electricity. Water for the station is collected from the Rangitata River by means of a 66km long irrigation race, which provides water for use by farms in summer, when demand for electricity is lower. In winter when electricity demand increases, and demand for irrigation water reduces, the water is used for power generation purposes. With an installed capacity of 25.2 MW, the Highbank scheme has an average annual output of 94 GWh. Highbank was previously grid connected (POC name : HBK0661 TRUS GG) but is now treated as embedded generation (POC name : HBK0661 TRUS EG behind ASB0661) for market purposes |  | www.trustpower.co.nz,EL Database, Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Highbank | 0
Hinemaiaia A | Hinemaiaia Hydro Scheme | Trustpower | Trustpower | Embedded | Hydro | 2.4 | Hydro | 0 | Not Applicable | 0 | 1939 | 1939 | 2.4 | 2.4 MW | 10 |  |  | 0 |  | WRK0331 | WTO - Waikato | NI - North Island | The Hinemaiaia scheme had it's beginnings in 1939 in the quest to develop an electric power supply for Taupo, with power eventually being generated in late 1952, and fed into the national grid in 1958. Fed by the Hinemaiaia River, the scheme today consists of 2,400kW HA, 1,350kW HB and 2,850kW HC stations giving a total annual output of 29.3GWh. The 33 hectare lake of the HA Station has an average depth of only 1.2m and contains 16.6 hours of storage at mean river flow. The river carries considerable pumice debris and the original lake was fully silted in it's first 25 years of existence. Levees have been built to form future silt ponds for the time when dredging of the lake area above the weir will become necessary to maintain storage. The HA lake is a wildlife sanctuary and has become the habitat of a wide variety of wild fowl. The lake in the past has been stocked with salvelinus fontinalis brook trout by the Wildlife Conservancy. The HA dam is comprised of an arch dam 12m deep in a narrow ignimbright gorge with an adjacent 90m long weir perched on the surface of the ignimbright rock with the intake structure situated on the left bank at the end of the weir. A remote controlled and hydraulically operated bypass gate has been placed in the dam which is capable of passing 5 cumecs when required. The intake chamber contains hydraulically operated bypass gates, intake screens and screen scraper mechanism. The screen scrapers cope with pumice debris and lake weed and the scraper operation is initiated by both pressure differential across the screen and time switch control. Two 243 metre long penstocks, one 1.67m in diameter and one 1.8m in diameter, lead from the intake chamber to the power station. The power station contains two horizontal shaft machines with Francis turbines |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Hinemaiaia | 0
Hinemaiaia B | Hinemaiaia Hydro Scheme | Trustpower | Trustpower | Embedded | Hydro | 1.35 | Hydro | 0 | Not Applicable | 0 | 1966 | 1966 | 1.35 | 1.35 MW | 6 |  |  | 0 |  | WRK0331 | WTO - Waikato | NI - North Island | Situated some 3km below the HC Station, the HB Station Dam is a 12 metre high arch dam in a narrow ignimbright gorge with a 75m long spillway weir adjacent. The 12.1 hectare lake provides independent storage from the HB station giving 7 hours storage at mean flow. From the intake structure with its gate and intake screen 360 metres of concrete conduit, 2.3 metres in diameter, and 168 metres of steel penstock conducts the water to the HB Power Station which houses a horizontal Francis turbine driving a 1350kW induction generator. |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Hinemaiaia | 0
Hinemaiaia C | Hinemaiaia Hydro Scheme | Trustpower | Trustpower | Embedded | Hydro | 2.85 | Hydro | 0 | Not Applicable | 0 | 1982 | 1982 | 2.85 | 2.85 MW | 13 |  |  | 0 |  | WRK0331 | WTO - Waikato | NI - North Island | The Hinemaiaia C dam has been built 2km down river from the HA Power Station in a very narrow ignimbright gorge some 27 metres deep. The lower section of the dam extends horizontally between the gorge walls while the the upper section has been designed as a buttressed wall. An ogee spillway has been incorporated into the dam structure to discharge flood waters and the weight counterbalanced radial gate controlling the impound waters self adjusts to spill flood waters. The 2 hectares of water confined in the lake provide negligible storage and the HC Station is operated in tandem with HA Station. |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Hinemaiaia | 0
Hokitika Diesel |  | Trustpower | Trustpower | Embedded | Thermal | 3.3 | Diesel | 0 | Not Applicable | 0 |  |  | 3.3 | 3.3 MW | 0.3 |  |  | 0 |  | KUM0661 | WEC - West Coast | SI - South Island | GWh and MW data estimated from Centralised Dataset. Reconciliation Manager generation end date 31/08/2007 |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Hokitika | 0
Hornby, Christchurch |  | Ravensdown Fertiliser Co-op | Meridian Energy | Embedded | Thermal | 0.7 | Unknown | 0 | Not Applicable | 0 |  |  | 0.7 | 0.7 MW | 1 |  |  | 0 |  | ISL0331 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Christchurch.Islington.Fertiliser | 0
Horotiu Landfill |  | Green Energy | WEL Networks | Embedded | Other | 0.9 | Biogas | 0 | Not Applicable | 0 | 2004 | 2004 | 0.9 | 0.9 MW | 7 |  |  | 0 |  | TWH0331 | WTO - Waikato | NI - North Island | It was expected that the landfill would be shut in 2006, but would to continue to produce gas for another 20 years |  | www.bioenergy.org.nz |  | No current series | 0
Horseshoe Bend | Teviot Hydro Scheme | Pioneer Generation | Trustpower | Partially Embedded | Hydro | 4.3 | Hydro | 0 | Not Applicable | 0 |  |  | 4.3 | 4.3 MW | 23 |  |  | 0 |  | CYD0331 | OTG - Otago/Southland | SI - South Island | Horseshoe Bend 23 annual GWh from Pioneer Generation fact sheet published on Central Lakes Trust website - based on Teviot total scheme 78 Gwh, with 55 under Teviot and the remaining 23 under Horseshoe Bend based on MW capacity |  | Electricity Commission,EMS (Reconciliation Manager List),www.centrallakestrust.org.nz | 1 | GEN.Hydro.HorseshoeBend | 0
Horseshoe Bend Wind |  | Pioneer Generation | Pioneer Generation | Embedded | Wind | 2.25 | Wind | 0 | Not Applicable | 0 | 2009 | 2009 | 2.25 | 0.75 MW | 8 | 3 x 0.75 MW |  | 0 |  | CYD0331 | OTG - Otago/Southland | SI - South Island | Situated adjacent to the Horseshoe Bend Hydro station the wind project consists of three 750kW NEG Micon wind turbines giving a maximum output of 2.25MW. The turbines have 45m high steel tubular towers and 44m diameter rotors giving an overall height of 69m. |  | www.pioneergen.co.nz |  | No current series | 0
Huntly |  | Genesis Energy | Genesis Energy | Grid Connected | Thermal | 500 | Coal_NI | 10300 | Gas | 10500 | 1983 | 1983 | 1000 | 250 MW | 2850 | 4 x 250 MW |  | 0 |  | HLY2201 | WTO - Waikato | NI - North Island | Each unit is capable of burning coal, natural gas or a combination of the two. Annual output of 5695GWh has been estimated based on actual output 2005-2006 calendar years less estimated Huntly p40 (total output for whole Huntly 2005+6 = 6030 GWh per annum average).Unit 4 was mothballed in December 2012. A second unit was mothballed late 2013, at which point Unit 4 was decommissioned. |  | www.genesisenergy.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.Huntly | HLY2201 HLY1
Huntly e3p |  | Genesis Energy | Genesis Energy | Grid Connected | Thermal | 400 | Gas | 7200 | Not Applicable | 0 | 2007 | 2007 | 400 | 400 MW | 2410 |  |  | 0 |  | HLY2202 | WTO - Waikato | NI - North Island | Annual output of 2410 GWh has been estimated based on same utilisation as Otahuhu B |  | www.genesisenergy.co.nz |  | GEN.Thermal.Huntly | HLY2201 HLY5
Huntly p40 |  | Genesis Energy | Genesis Energy | Grid Connected | Thermal | 48 | Gas | 9800 | Distillate | 9600 | Jun 2004 | 2004 | 48 | 48 MW | 335 |  |  | 0 |  | HLY2202 | WTO - Waikato | NI - North Island | Annual output of 335GWh has been estimated based on 80% utilisation |  | www.genesisenergy.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List), ACS data |  | GEN.Thermal.Huntly | 0
Indevin |  | Indevin | Trustpower | Embedded | Backup generation | 0 | Diesel | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island |  |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Blenheim.CloudyBay.Indevin | 0
Iwitahi |  | Radio New Zealand | Trustpower | Embedded | Unknown | 0.3 | Unknown | 0 | Not Applicable | 0 |  |  | 0.3 | 0.3 MW | 0 |  |  | 0 |  | WRK0331 | WTO - Waikato | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Iwitahi | 0
Jackson Estate |  | Jackson Estate | Trustpower | Embedded | Backup generation | 0.2 | Diesel | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0 |  |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island | GWh and MW data from Centralised Dataset |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Blenheim.Riverlands.Jackson | 0
Kaimai 5 | Kaimai Hydro Power Scheme | Trustpower | Trustpower | Embedded | Hydro | 0.35 | Hydro | 0 | Not Applicable | 0 | 1982 | 1982 | 0.35 | 0.35 MW | 2 | 1 x 0.35 MW |  | 0 |  | TGA0331 | BOP - Bay Of Plenty | NI - North Island |  |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Kaimai.1 | 0
Kaitawa | Waikaremoana | Genesis Energy | Genesis Energy | Grid Connected | Hydro | 36 | Hydro | 1.006 | Not Applicable | 0 | 1948 | 1948 | 36 | 18 MW | 91 | 2 x 18 MW |  | 0 |  | TUI1101 | HBY - Hawkes Bay | NI - North Island | The Waikaremoana Hydro Scheme is located between the remote Te Urewera National Park and Wairoa. The scheme includes the Kaitawa (36MW), Tuai (60MW), and Piripaua (42MW) hydro stations, and is centrally controlled from Tuai. Water from Lake Waikaremoana flows through the Kaitawa power station and into Lake Kaitawa before reaching the Tuai power station. From there it flows into the man-made Lake Whakamarino and through the Piripaua power station, before being released into the Waikaretaheke River and making its way to the sea. |  | www.genesisenergy.co.nz, Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Waikaremoana | 0
Kaniere Forks | Kaniere River | Trustpower | Trustpower | Embedded | Hydro | 0.43 | Hydro | 0 | Not Applicable | 0 | 1911 | 1911 | 0.43 | 0.43 MW | 4 |  |  | 0 |  | HKK0661 | WEC - West Coast | SI - South Island |  |  | www.trustpower.co.nz,Electricity Commission,EMS (Reconciliation Manager List) | 1 | GEN.Hydro.Hokitika.Kaniere.Forks | 0
Kapuni |  | Bay of Plenty Energy | Bay of Plenty Energy | Grid Connected Cogen | Cogeneration | 25 | Gas | 0 | Not Applicable | 0 | 1998 | 1998 | 25 | 10.3 MW | 130 | 2 x 10.3 MW, 1 x 3.2 MW, 1 x 1.5 MW |  | 0 |  | KPA1101 | TRN - Taranaki | NI - North Island | The plant provides heat and power for local industry. Some 490,000 tonnes of steam a year is also produced for use in the NGC Kapuni Gas Treatment Plant. This steam allows NGC's Benfield plants to strip carbon dioxide from Kapuni gas to maintain pipeline specifications. Steam excess to NGC's needs is transported via a dedicated 3 km long steam line to Lactose New Zealand's dairy processing plant. Units : Gas: 2 at 10.3 MW, steam: 1 at 3.2MW, 1 at 1.5 MW. The plant has a rated output of 25 MW. Of this 20 MW is exported to the national grid.The plant is owned by Bay of Plenty Energy and NGC as a joint venture |  | www.toddenergy.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) |  | NI.Kaponga.Import | 0
Karapiro | Waikato Hydro Scheme | Mighty River Power | Mighty River Power | Grid Connected | Hydro | 90 | Hydro | 0.265 | Not Applicable | 0 | May 1948 | 1948 | 90 | 30 MW | 525 |  |  | 14 |  | KPO1101 | WTO - Waikato | NI - North Island | As the last station on the Waikato River, Karapiro is required to release a minimum flow to maintain the water levels in the lower Waikato River. The required minimum flow means that at least two of the three generating units at Karapiro are typically operating at all times. Transmission lines connect the station with the national grid at Hamilton, as well as supplying sub-stations at Hinuera and Te Awamutu. |  | Electricity Commission,EMS (Reconciliation Manager List) | 8 | GEN.Hydro.Waikato.Karapiro | 0
Kawerau - BOP |  | Bay of Plenty Energy | Todd Energy | Partially Embedded | Geothermal | 6.4 | Geothermal | 0 | Not Applicable | 0 | 1989 | 1989 | 6.4 | 3.8 MW | 35 | 2 x 1.3 MW, 1 x 3.8 MW |  | 0 |  | KAW0111 | BOP - Bay Of Plenty | NI - North Island | TG1, the first of two developments, was commissioned in 1989 and generates 2.56 MW of electricity. It has two turbines, each driving a 1.3 MW generator. TG2, was commissioned in 1993 using two turbines to drive a single 3.8 MW generator. |  | www.toddenergy.co.nz,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List),www.nzgeothermal.org.nz |  | GEN.Geothermal.Kawerau.Tarawera | 0
Kawerau - CHH |  | Carter Holt Harvey | Carter Holt Harvey | Embedded | Cogeneration | 27 | Wood_waste | 0 | Not Applicable | 0 |  |  | 27 | 27 MW | 118 |  |  | 0 |  | KAW0111 | BOP - Bay Of Plenty | NI - North Island | Steam turbine from wood waste, turbine has capacity of 27MW however due to a lack of steam has been generating only 13.5MW |  |  |  | No current series | 0
Kawerau - KA24 |  | Geothermal Developments | Geothermal Developments | Embedded | Geothermal | 8.3 | Geothermal | 0 | Not Applicable | 0 | Sep 2008 | 2008 | 8.3 | 8.3 MW | 70 |  |  | 0 |  | KAW0111 | BOP - Bay Of Plenty | NI - North Island |  |  | www.nzgeothermal.org.nz |  | No current series | 0
Kawerau - TOPP 1 |  | Norske Skog Tasman | Norske Skog Tasman | Embedded | Geothermal | 25 | Geothermal |  | Not Applicable | 0 | Dec 2012 | 2012 | 25 | 25 MW | 210 |  |  | 0 |  | KAW0112 | BOP - Bay Of Plenty | NI - North Island |  |  | www.nzgeothermal.org.nz |  | No current series | #N/A
Kawerau - TPP |  | Norske Skog Tasman | Norske Skog Tasman | Grid Connected Cogen | Cogeneration | 37 | Gas | 0 | Not Applicable | 0 | 1966 | 1966 | 37 | 18.7 MW | 271 | 1 x 10 MW, 1 x 8 MW, 1 x 18.7 MW |  | 0 |  | KAW0112 | BOP - Bay Of Plenty | NI - North Island |  |  | PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) |  | No current series | 0
Kawerau Geothermal |  | Mighty River Power | Mighty River Power | Grid Connected | Geothermal | 100 | Geothermal | 0 | Not Applicable | 0 | 2008 | 2008 | 100 | 100 MW | 800 | 1 x 100 MW |  | 0 |  | KAW1101 | BOP - Bay Of Plenty | NI - North Island | Commissioned in November 2008 |  | EMS (Reconciliation Manager List) |  | GEN.Geothermal.Kawerau.Main | KAW1101 KAG0
Kew Hospital |  | Kew Hospital | Trustpower | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | INV0331 | OTG - Otago/Southland | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Invercargill.Hospital | 0
Kinleith |  | Genesis Energy | Carter Holt Harvey | Grid Connected Cogen | Cogeneration | 28 | Wood_waste | 0 | Gas | 11000 | 1998 | 1998 | 28 | 28 MW | 250 |  |  | 0 |  | KIN0112 | WTO - Waikato | NI - North Island | Maintained by Carter Holt Energy. This plant is located at the Carter Holt Harvey Pulp and Paper Plant at Kinleith, Tokoroa. It is fuelled by wood waste biomass supplemented as necessary with gas. The waste wood is a combination of bark, sawdust and chips, mainly pine with some eucalyptus. New Zealand biomass fuel is considered a renewable energy because it can be replenished by new plantations. The fuel is burnt in a boiler to produce steam for a 28MW steam turbine and for the pulp and paper mill. The bulk of the electricity generated is used on site. Carter Holt Harvey and Genesis Energy work closely to ensure a reliable steam supply for this major wood-processing site. The plant is owned by Genesis Energy, and Carter Holt Harvey operate and maintain the plant under contract to Genesis Energy. Engineering support for the plant is provided by the Genesis Energy engineering team based at Huntly Power Station. Total capacity is 28MW about 11% is from natural gas (about 3 MW) the rest is generated from Wood (about 25MW). |  | www.genesisenergy.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.Kinleith | 0
Kiwi Dairy, Hawera (Whareroa) |  | Todd Energy | Todd Energy | Grid Connected Cogen | Cogeneration | 69.6 | Gas | 9300 | Distillate | 0 | 1996 | 1996 | 69.6 | 26 MW | 180 | 4 x 10.9 MW, 1 x 26 MW |  | 0 |  | HWA1102 | TRN - Taranaki | NI - North Island | The Kiwi Cogeneration Station is located onsite at Fonterra's factory in Hawera, Taranaki and first entered production in 1996 as a gas-driven twin 10 MW turbine. A further two 10 MW turbines were later installed in conjunction with a 26 MW back pressure steam turbine. Gas is fed directly from the Kapuni production station, 22 kilometers, away via a dedicated pipeline. Note : Generation is metered at HWA1102 KIWI GG. For reconciliation generation is split equally between two buses HWA1102 TODD GG and HWA1102 MERI GG |  | www.toddenergy.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) |  | NI.Hawera.110KV.Whareroa.Import | HWA1102 WAA0
Kongahu |  | Buller Electricity | Simply Energy | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | ORO1101 | WEC - West Coast | SI - South Island |  |  | EMS (Reconciliation Manager List) |  | GEN.Unknown.Kongahu | 0
Kourarau |  | Genesis Energy | Genesis Energy | Partially Embedded | Hydro | 0.95 | Hydro | 0 | Not Applicable | 0 | 1923 | 1923 | 0.95 | 0.7 MW | 2 |  |  | 0 |  | MST0331 | WEL - Wellington | NI - North Island | The Kourarau Power Scheme has an installed generating capacity of 1100 KW, however, generation rarely exceeds 900 KW. The scheme was designed to meet the generating needs of some 235 consumers. The Kourarau Power Scheme does not feed directly into the national grid. The electricity is distributed throughout the Wairarapa area. Each station is fed by a small artificial reservoir formed by the damming of Kourarau Stream. Between each reservoir and the associated power station are sections of pipeline and penstocks that take water from the reservoir to a power station. Water from the Lower Power Station is discharged back into the natural channel of the Kourarau Stream. The Upper Dam and Reservoir were formed in 1925 by the damming of Kourarau Stream with an earth dam. The reservoir covers approximately 15 hectares. Water from the upper reservoir is taken through the Upper Power Station at a maximum rate of 290 litres per second. The upper reservoir has a normal operating range of 650 mm between minimum level and the spillway crest. During floods water that cannot be taken into the power station flows over the spillway and into the natural channel of Kourarau Stream. The Upper Power Station is a 200 KW (actual generator rating 250KW) station that uses a maximum flow of 290 litres per second to generate electricity. Water enters the Upper Power Station from the Upper Reservoir via a 785 metre long pipeline and single penstock system. A surge chamber is situated between the penstock and the pipeline to relieve pressure from the system that builds up due to fluctuating flows and generation patterns. The Lower Reservoir is 1.4 hectares in area and located downstream of the confluence of the Kourarau Stream and Sailormans Creek. The reservoir is formed by an earth dam, approximately 4 metres in height. Water enters the lake from the Upper Power Station tailrace and from the Kourarau Stream, including the flow from Sailormans Creek. The upper level of the lake is controlled by a fixed weir concrete-lined spillway. During floods, any water that cannot pass through the Lower Power Station, via the intake, flows over the spillway down the natural channel of Kourarau Stream. From the Lower Reservoir, water passes through a single 1182-metre pipeline to a surge tower. The pipeline then splits into two penstocks that carry water a further 2136 metres to the Lower Power Station. Water enters the two penstocks at a maximum rate of 900 litres per second. The Lower Power Station is a 900 KW station (actual generator rating 700 KW) situated adjacent to Kourarau Stream. Water then passes through a short tail-race before being discharged back into Kourarau Stream. |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Kourarau | 0
Kowhai | Teviot Hydro Scheme | Pioneer Generation | Pioneer Generation | Partially Embedded | Hydro | 1.9 | Hydro | 0 | Not Applicable | 0 | 2010 | 2010 | 1.9 | 1.9 MW | 5.5 |  |  | 0 |  | CYD0331 | OTG - Otago/Southland | SI - South Island | The station has a maximum generating capacity of 1.9MW and will produces an estimated 5.5GWh of energy each year. The site of the power station is approximately 3.5km east of Roxburgh adjacent to the Teviot Irrigation Company (TIC) Intake Weir on the Teviot River. The pipeline and penstock associated with the power station runs from the Marslin Dam some 1.5 km upstream. |  | www.pioneergen.co.nz |  | No current series | 0
Kumara | Dillmans Hydro Power Scheme | Trustpower | Trustpower | Embedded | Hydro | 6.5 | Hydro | 0 | Not Applicable | 0 | 1928 | 1928 | 6.5 | 6.5 MW | 30 |  |  | 0 |  | KUM0661 | WEC - West Coast | SI - South Island | This scheme had its beginnings in 1927, with power being generated for the first time in 1928. The scheme today consists of the Duffers Power Station, fed by races that in turn feed into the Kawhaka Creek, downstream artificial lake storage that in turn feeds the Dillmans Power Station, and the Kumara Power station fed by a race from Dillmans. With heads of 13 metres at Duffers, 46 metres at Dillmans and 78 metres at Kumara, and capacities of 500 kW, 3,500 kW and 6,500 kW respectively, the scheme has an average annual output of 47.9 GWh. |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Kumara.Kumara | 0
Kuratau |  | King Country Energy | King Country Energy | Embedded | Hydro | 6 | Hydro | 0 | Not Applicable | 0 | 1962 | 1962 | 6 | 3 MW | 30 | 2 x 3 MW |  | 0 |  | ONG0331 | CEN - Central | NI - North Island | Water is channeled down an open canal to a top screen with an earthquake gate from lake Kuratau. The two penstock pipes are both constructed from concrete until the surge chamber, from there on they are steel, each one feeds it's own turbine. Station Statistics: Location: Hydro Rd, Kuratau. Head:64 metres. Turbines: Boving Horizontal Francis (x 2), Generator:2 x ASEA , 3 MW at 600 rpm. Station Mean Output: 30 GWh |  | www.toddenergy.co.nz,EL Database,EMS (Reconciliation Manager List) |  | GEN.Hydro.Kuratau | 0
Lake Grassmere |  | Energy3 | Meridian Energy | Embedded | Wind | 0.66 | Wind | 0 | Not Applicable | 0 | 2014 | 2014 | 0.66 | 0.66 MW | 6 | 1 x 0.66 MW |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island | Annual output estimated based on 40% utilisation |  | www.windenergy.org.nz/lake-grassmere |  | No current series | #N/A
Lloyd Mandeno | Kaimai Hydro Power Scheme | Trustpower | Trustpower | Embedded | Hydro | 15.6 | Hydro | 0 | Not Applicable | 0 | 1972 | 1972 | 15.6 | 7.8 MW | 70 | 2 x 7.8 MW |  | 0 |  | TGA0331 | BOP - Bay Of Plenty | NI - North Island | Lloyd Mandeno is the most up-stream station in the Kaimai scheme. A lake has been formed by building a 29m earth dam across the Mangaonui valley, this creates the main ponding reservoir for the station. The Lake has a surface area of 8.1ha and an operating range of 3m. There are 9 km of diversion tunnels in this part of the scheme. Water flows from the lake into the canal through a feed tunnel that is regulated to maintain a constant water level in the canal and constant head on the machines. In the power station there are two sets of turbines and generators, each producing 7,800kW at 11,000 volts. Operating speed is 750rpm and each set uses 6.1 cubic metres per second at full load. |  | www.trustpower.co.nz,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Kaimai.1 | 0
Lower Mangapapa | Kaimai Hydro Power Scheme | Trustpower | Trustpower | Embedded | Hydro | 6 | Hydro | 0 | Not Applicable | 0 | 1979 | 1979 | 6 | 6 MW | 17 |  |  | 0 |  | TGA0331 | BOP - Bay Of Plenty | NI - North Island | The Lower Mangapapa Power Station is situated on the right bank of the Mangapapa River 4km further downstream from Lloyd Mandeno. The station was constructed after the summer of 1976 and was completed in the April of 1979. This section has a concrete arch dam built across a narrow gorge in the Mangapapa River. The dam is 26m high forming a lake that extends upstream to the Lloyd Mandeno station. Water is taken from the lake through a 3m diametre concrete lined tunnel 400 m in length. A steel tunnel outlet into the station divides to supply two horizontal turbines which drive a centrally located 6,000 kW induction generator. The combined output of the turbines is 6250kW at 32.8m head. The unit has an operating speed of 375rpm and a water consumption of 21.5 cubic metres per second. The average energy produced is 16.7 GWh per year. |  | www.trustpower.co.nz,EMS (Reconciliation Manager List) |  | GEN.Hydro.Kaimai.1 | 0
Lulworth Wind |  | Energy3 | Meridian Energy | Embedded | Wind | 1 | Wind | 0 | Not Applicable | 0 | 2011 | 2011 | 1 | 0.25 MW | 3.2 | 4 x 0.25 MW |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island | Energy3 installed four secondhand Micon 530 wind turbines at the site. The turbines have a capacity of 250kW each, giving the wind farm a capacity of 1 MW. |  | windenergy.org.nz |  | No current series | 0
Mahinerangi |  | Trustpower | Trustpower | Embedded | Wind | 36 | Wind | 0 | Not Applicable |  | 2011 | 2011 | 36 | 3 MW | 112 | 12 x 3 MW |  | 0 |  | HWB0331 | OTG - Otago/Southland | SI - South Island | Mahinerangi is currently metered as part of Waipori local output. |  | www.trustpower.co.nz |  | SI.Dunedin.HalfwayBush.Local | 0
Manapouri |  | Meridian Energy | Meridian Energy | Grid Connected | Hydro | 850 | Hydro | 1.5 | Not Applicable | 0 | 1972 | 1972 | 850 | 120 MW | 5100 |  |  | 382 |  | MAN2201 | OTG - Otago/Southland | SI - South Island | The power station is located underground within Fiordland National Park. The turbines, generators and other equipment are contained in the powerhouse located in an underground cavern. The cavern was cut from solid rock and is 111 metres long, 18 metres wide and 39 metres high. Vehicles can drive down to the powerhouse through an access tunnel which is more than two kilometres long. It descends at a 1-in-10 gradient, and is wide enough to allow vehicles to pass. The powerhouse can also be reached by an elevator which descends 220 metres (equivalent to a 70-storey building) in two-and-a-half minutes. Uses 178 metre height difference between Lake Manapouri and the sea at Deep Cove. Once water has passed through turbines it leaves the station through two 10 kilometre-long tunnels to Deep Cove. The station was originally built with only one tailrace tunnel, but a second tunnel was commissioned in 2002. Reconditioning of the plant and the new tail race have resulted in an increase in maximum output, although actual output is constrained by resource management requirements. |  | www.meridianenergy.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List),ACS data |  | GEN.Hydro.Manapouri | 0
Mangahao |  | Todd Energy | Todd Energy | Grid Connected | Hydro | 42 | Hydro | 2.299 | Not Applicable | 0 | 1924 | 1924 | 42 | 26 MW | 136 | 1 x 26 MW, 2 x 5.7 MW, 1 x 4 MW |  | 5 |  | MHO0331 | CEN - Central | NI - North Island | The water stored in the reservoirs formed by the two dams on the Mangahao river is brought by a 1.6km long tunnel to the third reservoir on the Tokomaru stream and then to the surge chamber by a 2.1km tunnel. The headwaters of the Mangahao River are a major tributary of the Manawatu River. The total catchment area of the scheme is 86 square kilometers in an area of high annual rainfall, which on average exceeds 3,700 millimeters. Location: East road, Shannon. Average Annual Output: 126 GWh, Total MW rating : 38 MW, Head 271 meters. Turbines Francis Type: 26 MW at 7250 rpm, Pelton-wheel Type:2 at 6 MW at 375 rpm Generators 1 machine of 28.9 MW at 11,000 volts, 2 machines of 6 MW at 11,000 volts. An addition mini hydro station added 4 MW in 2004. Mini Hydro Stats: Average Annual Output: 10 GWh, Total MW rating : 4 MW. King Country Energy, in conjunction with Todd Energy, acquired this generation plant in 1997. (50/50 joint venture). (As at 20/5/2012 ownership of this plant was to be fully transferred to KCE subject to regulatory and shareholder approval) |  | www.toddenergy.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Mangahao | 0
Mangahewa |  | Todd Energy | Todd Energy | Embedded | Thermal | 9 | Gas | 0 | Not Applicable | 0 | Feb 2009 | 2009 | 9 | 9 MW | 50 |  |  | 0 |  | HUI0331 | TRN - Taranaki | NI - North Island |  |  | Todd Energy via email |  | No current series | 0
Mangapehi |  | Clearwater Hydro | Mighty River Power | Embedded | Hydro | 1.6 | Hydro | 0 | Not Applicable | 0 | 2008 | 2008 | 1.6 | 0.8 MW | 5 | 2 x 0.8 MW |  | 0 |  | HTI0331 | WTO - Waikato | NI - North Island |  |  | EMS (Reconciliation Manager List), CDS, www.clearwaterhydro.co.nz |  | GEN.Hydro.Mangapehi | 0
Mangatangi Dam |  | Watercare Services | Mighty River Power | Partially Embedded | Hydro | 0.6 | Hydro | 0 | Not Applicable | 0 |  |  | 0.6 | 0.6 MW | 5 |  |  | 0 |  | BOB0331 | AKL - Auckland | NI - North Island | At Mangatangi, power from the generator is used to run compressors that pump air into the dam water. Air is pumped into the dam water to reduce the risk of algae growing in the dam. At Waitakere, the generator powers the treatment plant. |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Auckland.Mangatangi | 0
Mangatawhiri |  | Counties Power | Mighty River Power | Embedded | Hydro | 0.2 | Hydro | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0.3 |  |  | 0 |  | BOB0331 | AKL - Auckland | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Auckland.Mangatawhiri | 0
Mangorei |  | Trustpower | Trustpower | Embedded | Hydro | 4.5 | Hydro | 0 | Not Applicable | 0 | 1906 | 1906 | 4.5 | 1.3 MW | 21 | 1 x 0.6 MW, 3 x 1.3 MW |  | 0 |  | CST0331 | TRN - Taranaki | NI - North Island | Originally constructed in 1904 to use water from the Waiwakaiho River, the Mangorei Power Station first supplied power in 1906 - for street lighting in New Plymouth and 41 customers. A steady increase in demand for electricity resulted in plans to store water for generation purposes behind a dam across the Mangamahoe Stream, with work finally starting in 1930. Said at the time of it's completion in 1931 to be the highest earth dam in Australiasia, the 25 metre high dam supplies water via two tunnels to one 600kW and three 1300kW horizontal turbines. With a total capacity of 4,500 kW, the Mangorei power scheme has an average annual output of 20.9 GWh. |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Mangamahoe | 0
Mansons Developments |  | Mighty River Power | Mighty River Power | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0.002 MW | 0 |  |  | 0 |  | PEN1101 | AKL - Auckland | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Auckland.Mansons.MountRoskill | 0
Maraetai | Waikato Hydro Scheme | Mighty River Power | Mighty River Power | Grid Connected | Hydro | 360 | Hydro | 0.498 | Not Applicable | 0 | Feb 1971 | 1971 | 360 | 36 MW | 885 |  |  | 0 |  | MTI2201 | WTO - Waikato | NI - North Island | 'The two power stations ( A + B) have the largest capacity of any of the stations of the Waikato hydro system. The generating units in the Maraetai B have sophisticated frequency control and time - error corrections equipment allowing this powerhouse to be used for frequency keeping - they respond to the ebb and flow of power on the national grid in order to maintain a constant current and voltage. |  | Electricity Commission,EMS (Reconciliation Manager List) | 5 | GEN.Hydro.Waikato.Maraetai | 0
Maraetai Embedded |  | Mighty River Power | Mighty River Power | Embedded | Hydro | 0.1 | Hydro | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0 |  |  | 0 |  | WKM2201 | WTO - Waikato | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Waikato.Maraetai.1KV | 0
Marlborough Lines Diesel |  | Marlborough Lines | Trustpower | Embedded | Thermal | 9 | Diesel | 0 | Not Applicable | 0 |  |  | 9 | 9 MW | 0 |  |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island | Primarily backup/peak management plant with peak of 9 MW from CDS. Discountinued from June 2006 so assumed Gwh = 0. Marlborough Lines have indicated that they expect to purchase 1 MW of portable generation in the 2006/2007 year (2006 Annual Repor |  | Electricity Commission,EMS (Reconciliation Manager List), Marlborough Lines Annual Report 2006, CDS |  | GEN.Thermal.Blenheim.33KV.NomadicDiesel.11KV | 0
Marlborough Lines Diesel II |  | Marlborough Lines | Trustpower | Embedded | Thermal | 0 | Diesel | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | BLN0332 | NEL - Nelson/Marlbourough | SI - South Island | Reconciliation Manager generation end date 31/08/2007 |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Blenheim.33KV.NomadicDiesel.1KV | 0
Marokopa Power Station |  | Marakopa Generation | Contact Energy | Embedded | Hydro | 0.1 | Hydro | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0.6 |  |  | 0 |  | HTI0331 | WTO - Waikato | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Marokopa | 0
Marsden B |  | Mighty River Power | Mighty River Power | Grid Connected | Thermal | 0 | Coal_NI | 0 | Not Applicable | 0 | 1979 | 1979 | 236 | 236 MW | 0 |  |  | 0 |  | MDN1101 | NIS - North Isthmus | NI - North Island | Mothballed. As at April 2012 the plant had been dismantled, pending shipment to an overseas buyer | 2012 | EL Database,EMS (Reconciliation Manager List), www.mightyriverpower.co.nz |  | GEN.Thermal.Marsden.B | 0
Marsden Diesel |  | Trustpower | Trustpower | Embedded | Thermal | 9 | Diesel | 0 | Not Applicable | 0 | 2011 | 2011 | 9 | 1.8 MW | 0 | 5 x 1.8 MW |  | 0 |  | BRB0331 | NIS - North Isthmus | NI - North Island | Caterpillar diesel units used as peaking plant to mitigate price peaks. The plant is operated remotely from Tauranga. |  | www.trustpower.co.nz, www.energynews.co.nz |  | No current series | 0
Matahina |  | Trustpower | Trustpower | Grid Connected | Hydro | 72 | Hydro | 0.541 | Not Applicable | 0 | 1967 | 1967 | 72 | 36 MW | 280 | 2 x 36 MW |  | 7 |  | MAT1101 | BOP - Bay Of Plenty | NI - North Island | 5 kilometres south of Whakatane, the Matahina earth dam is New Zealand's second largest. It is 86 metres high, built on 24 metre deep foundations, 365 metres wide at its base, and 396 metres long. The 3.8 million cubic metres (3.8 billion litres) of water behind the dam drive two 50,000 hp turbines that in turn drive two 36 MW generators producing an average annual output of approximately 300 GWh. The station was commissioned in 1967, but was damaged in the 1987 Edgecumbe earthquake and extensive strengthening work was subsequently undertaken. In 1999 TrustPower purchased the Station from ECNZ for $115 million. An eel pass has been constructed over the dam to allow young eels to migrate upstream. |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Matahina | 0
Mataura |  | Niblick Trust | Simply Energy | Embedded | Hydro | 0.9 | Hydro | 0 | Not Applicable | 0 |  |  | 0.9 | 0.9 MW | 4.5 |  |  | 0 |  | GOR0331 | OTG - Otago/Southland | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Mataura | 0
Matawai |  | Clearwater Hydro | The Lines Compnay | Embedded | Hydro | 2 | Hydro |  | Not Applicable | 0 | Aug 2009 | 2009 | 2 | 1 MW | 10 | 2 x 1 MW |  | 0 |  | GIS0501 | HBY - Hawkes Bay | NI - North Island | A.K.A. Waikohu hydro scheme |  | www.gisborneherald.co.nz, www.clearwaterhydro.co.nz |  | No current series | 0
Maungatapere |  | Trustpower | Trustpower | Embedded | Thermal | 0.5 | Unknown | 0 | Not Applicable | 0 |  |  | 0.5 | 0.5 MW | 0.3 |  |  | 0 |  | MPE0331 | NIS - North Isthmus | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Maungatapere | 0
McKays Creek | Kaniere River | Trustpower | Trustpower | Embedded | Hydro | 1.1 | Hydro | 0 | Not Applicable | 0 | 1931 | 1931 | 1.1 | 1.1 MW | 8 |  |  | 0 |  | HKK0661 | WEC - West Coast | SI - South Island |  |  | www.trustpower.co.nz,Electricity Commission,EMS (Reconciliation Manager List) | 2 | GEN.Hydro.Hokitika.Kaniere.McKaysCreek | 0
McKee |  | Todd Energy | Todd Energy | Grid Connected | Thermal | 102 | Gas | 0 | Not Applicable | 0 | 2013 | 2013 | 102 | 50 MW | 300 | 2 x 50 MW, 2 x 2 MW |  | 0 |  | MKE1101 | TRN - Taranaki | NI - North Island | Two 50MW gas turbines and 2 x 1 MW cogen units. GWh estimated based on CDS data. |  | www.toddenergy.co.nz |  | GEN.Thermal.Mangahewa.Grid | #N/A
Middleton |  | CWF Hamilton & Co | Meridian Energy | Embedded | Unknown | 0.2 | Unknown | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0 |  |  | 0 |  | ISL0331 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Christchurch.Islington.Middleton | 0
Milburn |  | Department of Corrections | Meridian Energy | Embedded | Thermal | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | BAL0331 | OTG - Otago/Southland | SI - South Island |  |  | EMS (Reconciliation Manager List) |  | GEN.Thermal.Milburn | 0
Mill Creek |  | Meridian Energy | Meridian Energy | Embedded | Wind | 71.3 | Wind | 0 | Not Applicable | 0 | Nov 2014 | 2014 | 59.8 | 2.3 MW | 235 | 26 x 2.3 MW |  | 0 |  | WIL0331 | WEL - Wellington | NI - North Island | First electricity generated May 2014. Covers approx 18 km2, using Seimens turbines |  | https://www.meridianenergy.co.nz/about-us/mill-creek/ |  | No current series | #N/A
Mokai I,II & III |  | Tuaropaki Power Company | Mighty River Power | Grid Connected | Geothermal | 112 | Geothermal | 0 | Not Applicable | 0 | Feb 2000 | 2000 | 112 | 35 MW | 900 |  |  | 0 |  | WKM2201 | WTO - Waikato | NI - North Island | The Mokai power station was commissioned in February 2000, and is owned by the Tuaropaki Power Company. Mighty River Power is contracted to operate and maintain the station. The Mokai station is basically a larger version of the plant at Rotokawa, with a nominal generation capacity of 94MW. The station was upgraded by an additional 17MW in August 2007 Like Rotokawa, Mokai’s generating plant consists of a main steam back pressure turbine and an ORMAT binary plant . Mokai is modelled as a grid connected network for the purposes of market reconciliation |  | EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List), www.mightriverpower.co.nz |  | GEN.Geothermal.Mokai | WKM2201 MOK0
Mokauiti |  | King Country Energy | King Country Energy | Embedded | Hydro | 1.9 | Hydro | 0 | Not Applicable | 0 | 1963 | 1963 | 1.9 | 1.3 MW | 7 | 1 x 1.3 MW, 1 x 0.6 MW |  | 0 |  | ONG0331 | CEN - Central | NI - North Island | The original power station was commissioned on the Mokau River beside the Wairere Falls in 1925 (turbine 1) with just one machine giving an output of 490 kilowatts. Later three more machines were added in 1938 (turbine 2), 1952 (turbine 3) and 1981 (turbine 4) with associated penstocks, buildings and tailraces. The pipeline runs from a pond interrupting the Mokauiti Stream, a tributary of the Mokau river. |  | www.toddenergy.co.nz,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Mokauiti | 0
Mokoia Road, Hawera |  | Swift Energy | Genesis Energy | Embedded | Thermal | 0.2 | Unknown | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0.4 |  |  | 0 |  | HWA0331 | TRN - Taranaki | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Mokoia | 0
Monowai |  | Pioneer Generation | Trustpower | Embedded | Hydro | 6.6 | Hydro | 0 | Not Applicable | 0 | May 1925 | 1925 | 6.6 | 2.2 MW | 40 | 3 x 2 MW |  | 0 |  | NMA0331 | OTG - Otago/Southland | SI - South Island |  |  | Electricity Commission,EMS (Reconciliation Manager List),www.med.govt.nz, www.centrallakestrust.org.nz |  | GEN.Hydro.Monowai | 0
Montalto | Rangitata Diversion Race | Trustpower | Trustpower | Partially Embedded | Hydro | 1.8 | Hydro | 0 | Not Applicable | 0 | 1982 | 1982 | 1.8 | 1.8 MW | 12 |  |  | 0 |  | ASB0331 | CAN - Canterbury | SI - South Island | The Montalto Power Scheme had it's beginnings in 1958, when design work started on a project to generate electricity utilising the stepped flow of the Rangitata Diversion Race - an irrigation project completed in the early 1940's. Commissioning of the Montalto Power Station, which produces 1,100kW during irrigation season and 1,800 kW at other times was completed in 1982. Today the station has an annual output of 12GWh. |  | www.trustpower.co.nz,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Montalto.11KV | 0
Motukawa |  | Trustpower | Trustpower | Embedded | Hydro | 4.5 | Hydro | 0 | Not Applicable | 0 | Jan 1927 | 1927 | 4.8 | 1.5 MW | 26 |  |  | 0 |  | HUI0331 | TRN - Taranaki | NI - North Island | Commissioned in January of 1927, the Motukawa scheme uses 99 of an available 122 metre difference in elevation between the Manganui River near Tariki and the Waitara River near Motukawa to drive three generating sets, the last of which was added in 1938. To provide temporary power during construction a 200kVA hydro plant, the remains of which still exist today, was constructed at the headworks near Tariki. With a total capacity of 4,800 kW, the Motukawa scheme has an average annual output of 25.8 GWh. |  | www.trustpower.co.nz,Electricity Commission,EMS (Reconciliation Manager List), ACS data |  | GEN.Hydro.Motukawa | 0
Mount Stuart |  | Pioneer Generation | Pioneer Generation | Embedded | Wind | 7.65 | Wind | 0 | Not Applicable | 0 | Nov 2011 | 2011 | 7.65 | 0.85 MW | 25.6 |  |  | 0 |  | BAL0331 | OTG - Otago/Southland | SI - South Island | The wind farm has 9 wind turbines, with a combined generating capacity of 7.65MW. The 850kW turbines are supplied by Gamesa, a wind turbine manufacture based in Spain. The turbines have a 45 metre tower, and their blades have a 52 metre diameter. Mt Stuart is the first wind farm in New Zealand and Australia to use Gamesa turbines. Pioneer began construction of the wind farm in April 2011. The wind farm was commissioned in November 2011. The wind farm produces about 25,600MWh per year and feeds its electricity into the OtagoNet network. |  | http://windenergy.org.nz |  | No current series | 0
Mud House |  | Kiwi Wine Company | Trustpower | Embedded | Backup generation | 0.2 | Diesel | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0 |  |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island |  |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Blenheim.Riverlands.MudHouse | 0
New Plymouth |  | Contact Energy | Contact Energy | Grid Connected | Thermal | 0 | Gas | 11000 | Fuel_Oil | 11000 | 1974 | 1974 | 360 | 105 MW | 0 |  |  | 0 |  | NPL1101 | TRN - Taranaki | NI - North Island | 'The plant is now mothballed following the discovery of asbestos in the plant earlier in 2007. The first of the station's five generating units was commissioned in 1974. It injected into the grid on two buses (110kv and 200kv, NPL1101 and NPL2201, 2 units and 1 unit respectively). The station's 198 metre chimney is one of the tallest in New Zealand and contains one million bricks, 16,400 tonnes of concrete and 1,200 tonnes of reinforcing steel. It is designed to sway between five and eight cm during 40 to 60 knot winds. | 2011 | www.mycontact.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List), ACS data |  | GEN.Thermal.NewPlymouth.110KV,GEN.Thermal.NewPlymouth.220KV | 0
Nga Awa Purua |  | Mighty River Power | Mighty River Power | Grid Connected | Geothermal | 140 | Geothermal | 0 | Not Applicable | 0 | 2010 | 2010 | 140 | 140 MW | 1100 | 1 x 140 MW |  | 0 |  | NAP2201 | WTO - Waikato | NI - North Island | The generation plant was developed by Mighty River Power in partnership with the Tauhara North No 2 Trust. It is close to the existing Rotokawa geothermal power station and connects into existing 220kv transmission lines directly over the field. |  | http://www.mightyriverpower.co.nz/Generation/ |  | GEN.Geothermal.Rotokawa.Grid | NAP2201 NAP0
Ngahere |  | Birchfield Minerals | Mighty River Power | Embedded | Hydro | 0.1 | Hydro | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0.2 |  |  | 0 |  | DOB0331 | WEC - West Coast | SI - South Island |  |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Ngahere | 0
Ngatamariki |  | Mighty River Power | Mighty River Power | Grid Connected | Geothermal | 82 | Geothermal |  | Not Applicable | 0 | Mar 2013 | 2013 | 82 | 21 MW | 670 | 4 x 21 MW |  | 0 |  | NAP2202 | WTO - Waikato | NI - North Island | While Mighty River wholly ownes the power station, the Tauhara North No. 2 Trust receives a revenue stream from the operation of the plant, and has the option to take a market-value equity stake in the power station after its first 10 years of operation. |  | www.mightyriver.co.nz |  | GEN.Geothermal.Ngatamariki | #N/A
Ngawha |  | Top Energy | Top Energy | Embedded | Geothermal | 25 | Geothermal | 0 | Not Applicable | 0 | Jun 1998 | 1998 | 25 | 12 MW | 200 |  |  | 0 |  | KOE0331 | NIS - North Isthmus | NI - North Island | Located approximately seven kilometers from Kaikohe, the Ngawha Geothermal Power Station was set up to use geothermal energy from the Ngawha Springs area to generate electricity. Using four of twenty existing wells drilled by the Ministry of Works in the early 1980's, the plant uses a binary-generating unit manufactured by Ormat Industries of Israel. Operation commenced in June 1998. |  | PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Geothermal.Ngawha | 0
Ohaaki |  | Contact Energy | Contact Energy | Grid Connected | Geothermal | 70 | Geothermal | 0 | Not Applicable | 0 | 1989 | 1989 | 116 | 58 MW | 300 |  |  | 0 |  | OKI2201 | WTO - Waikato | NI - North Island | Production wells at Ohaaki are, on average, 1.2 km deep and reach water at temperatures up to 280°C. The most distinctive feature at Ohaaki is the 105 metre high cooling tower. Using natural convection, the tower cools the water used to condense the steam as it exits the power turbines. Although Ohaaki still has 116 MWe of plant installed on site, high pressure turbines are now decommissioned and only one of the two remaining turbines is operating. The station generates between 30 and 40 MWe due to field limitations. Some additional Ohaaki drilling has been undertaken to fully load the remaining turbine. |  | EL Database,PB 'Thermal & Geothermal Generation Capabilities',EMS (Reconciliation Manager List),www.nzgeothermal.org.nz |  | GEN.Geothermal.Ohaaki | OKI2201 OKI0
Ohakuri | Waikato Hydro Scheme | Mighty River Power | Mighty River Power | Grid Connected | Hydro | 112 | Hydro | 0.278 | Not Applicable | 0 | Feb 1962 | 1962 | 112 | 28 MW | 400 |  |  | 14 |  | OHK2201 | WTO - Waikato | NI - North Island | Ohakuri has an earth dam with concrete gravity sections for the intake and spillway structures. Steel penstocks lead from the intake to the four Francis turbines in the powerhouse. An auxiliary turbine takes water through a dedicated penstock to generate electricity for the station. An open concrete spillway sweeps around the right end of the dam and down to the river below. A special feature is the fantail-shaped outlet which throws the water in a high, wide arc to minimise any erosion while the gates are open. The powerhouse lies below the dam on the left bank. For 1 MW of electricity to be generated at this station, 3.6 tonnes of water every second is required. Each of the four generators produces electricity at 11,000 volts. Transformers step up the voltage to 220,000 volts for transmission over the national grid. |  | Electricity Commission,EMS (Reconciliation Manager List) | 2 | GEN.Hydro.Waikato.Ohakuri | 0
Ohau A | Waitaki Hydro Scheme | Meridian Energy | Meridian Energy | Grid Connected | Hydro | 264 | Hydro | 0.501 | Not Applicable | 0 | 1980 | 1980 | 264 | 66 MW | 1150 |  |  | 0 |  | OHA2201 | SCN - South Canterbury | SI - South Island | Water flowing from Lake Pukaki enters the Pukaki canal or can be spilled into the normally dry Pukaki Riverbed. Water flowing down the Pukaki canal merges with the Ohau Canal just before the Ohau A station, the Pukaki River flows to Lake Benmore. After passing through Ohau A the water flows into Lake Ruataniwha. |  | www.meridianenergy.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) | 3 | GEN.Hydro.Waitaki.Ohau.A | 0
Ohau B | Waitaki Hydro Scheme | Meridian Energy | Meridian Energy | Grid Connected | Hydro | 212 | Hydro | 0.417 | Not Applicable | 0 | 1984 | 1984 | 212 | 53 MW | 970 |  |  | 0 |  | OHB2201 | SCN - South Canterbury | SI - South Island |  |  | www.meridianenergy.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) | 4 | GEN.Hydro.Waitaki.Ohau.B | 0
Ohau C | Waitaki Hydro Scheme | Meridian Energy | Meridian Energy | Grid Connected | Hydro | 212 | Hydro | 0.42 | Not Applicable | 0 | 1985 | 1985 | 212 | 53 MW | 970 |  |  | 0 |  | OHC2201 | SCN - South Canterbury | SI - South Island | Ohau C is situated downstream of Ohau B on a canal that links Lakes Ruataniwha and Benmore. A complex series of weirs allows water to be diverted from the canal into the nearby Ohau River (that also flows to Lake Benmore) allowing Ohau B to continue operating when Ohau C is out of action. |  | www.meridianenergy.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) | 5 | GEN.Hydro.Waitaki.Ohau.C | 0
Omarama |  | Waitaki Power | Meridian Energy | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | WTK0331 | OTG - Otago/Southland | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Omarama | 0
Onekaka |  | Onekaka Energy | Onekaka Energy | Embedded | Hydro | 1 | Hydro | 0 | Not Applicable | 0 |  |  | 1 | 1 MW | 3.2 |  |  | 0 |  | MPI0661 | NEL - Nelson/Marlbourough | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Onekaka | 0
Opuha |  | Alpine Energy | Contact Energy | Partially Embedded | Hydro | 7.5 | Hydro | 0 | Not Applicable | 0 | 1999 | 1999 | 7.5 | 7.5 MW | 21 |  |  | 0 |  | ABY0111 | SCN - South Canterbury | SI - South Island |  |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Opuha | 0
Opunake |  | Trustpower | Trustpower | Embedded | Hydro | 0.3 | Hydro | 0 | Not Applicable | 0 |  |  | 0.3 | 0.3 MW | 1.2 |  |  | 0 |  | OPK0331 | TRN - Taranaki | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Opunake | 0
Orion Diesel |  | Orion | Orion | Embedded | Thermal | 0.3 | Diesel | 0 | Not Applicable | 0 |  |  | 0.3 | 0.3 MW | 0.1 |  |  | 0 |  | ADD0661 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Addington.66KV.NomadicDiesel.1 | 0
Orion Diesel II |  | Orion | Orion | Embedded | Thermal | 0.2 | Diesel | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0 |  |  | 0 |  | ADD0661 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Addington.66KV.NomadicDiesel.2 | 0
Otahuhu A |  | Contact Energy | Contact Energy | Grid Connected | Thermal | 0 | Gas | 15500 | Not Applicable | 0 | 1968 | 1968 | 55 | 55 MW | 0 |  |  | 0 |  | OTA1101 | AKL - Auckland | NI - North Island | The first four units of Otahuhu A were commissioned in 1968. At the time it was the first large gas turbine power station in Australasia. Because of age and low thermal efficiency the plant is now only ever operated for emergency reasons. Two of the three available units were operated to provide 'reactive power' for the electricity transmission system. Plant site to be decommisioned along with Otahuhu B | 2015 | EL Database,Electricity Commission,EMS (Reconciliation Manager List), www.med.govt.nz |  | GEN.Thermal.Otahuhu.A | 0
Otahuhu B |  | Contact Energy | Contact Energy | Grid Connected | Thermal | 0 | Gas | 7450 | Not Applicable | 0 | Jan 2000 | 2000 | 380 | 380 MW | 0 |  |  | 0 |  | OTA2202 | AKL - Auckland | NI - North Island | Otahuhu B capacity varies with the source of the data. The 380 MW figure comes from Contact Energy's website. Transpower reserve modelling documentation lists OTAB's capacity at 395 MW. ACS data has capacity at 372 MW. Plant ceased operation September 2015. | 2015 | EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.Otahuhu.B | 0
Otematata |  | Network Waitaki | Meridian Energy | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | OTT0011 | OTG - Otago/Southland | SI - South Island | Located at Kurow |  | EMS (Reconciliation Manager List) |  | GEN.Unknown.Kurow | 0
Oxburn/Glenorchy |  | Pioneer Generation | Pioneer Generation | Embedded | Hydro | 0.4 | Hydro | 0 | Not Applicable | 0 | 1968 | 1968 | 0.4 | 0.4 MW | 2 | 2 x 0.5 MW |  | 0 |  | FKN0331 | OTG - Otago/Southland | SI - South Island |  |  | Electricity Commission,EMS (Reconciliation Manager List),www.qldc.govt.nz |  | GEN.Hydro.Glenorchy | 0
Pacific Steel |  | Vector | Trustpower | Embedded | Backup generation | 0.2 | Unknown | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0 |  |  | 0 |  | MNG0331 | AKL - Auckland | NI - North Island | Peak injection of 170kw for 2006/07 from CDS |  | EMS (Reconciliation Manager List),CDS |  | GEN.Thermal.Mangere.SteelMill | 0
Paerau | Paerau Gorge Power Scheme | Trustpower | Trustpower | Embedded | Hydro | 10 | Hydro | 0 | Not Applicable | 0 | 1984 | 1984 | 10 | 5 MW | 48 | 2 x 5 MW |  | 0 |  | NSY0331 | OTG - Otago/Southland | SI - South Island | The combined power and irrigation scheme operates by diverting the Taieri River's flow at Paerau using a substantial weir structure in the river which maintains the water level into the scheme while allowing floods and a minimum river flow to pass. The scheme's inflow passes along an aquaduct through substantial cuttings and a 1.3 kilometre long tunnel before feeding the Paerau Power Station. The outflow from the power station fills a large ponding area from which the irrigation scheme and Patearoa Power Station draw. The irrigation scheme now extends for 35 kilometres down the western side of Maniototo basin. The east side proposal is limited to the second power station near Patearoa which discharges back into the Taieri river. When low flows occur during summer, supplementary flows will be released from the Loganburn Reservoir formed at the site of Great Moss Swamp to ensure minimum river flows are maintained and that sufficient irrigation water is available to the scheme. |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Paerau | 0
Palmerston Nth Mini Hydro |  | Palmerston North City Council | Mighty River Power | Embedded | Hydro | 0 | Hydro | 0 | Not Applicable | 0 |  |  | 0 | 0.02 MW | 0 |  |  | 0 |  | BPE0331 | CEN - Central | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.PalmerstonNorth.Turitea.Bunnythorpe | 0
Pan Pac |  | Pan Pac Forest Products | Pan Pac Forest Products | Embedded | Cogeneration | 12.8 | Wood_waste |  | Not Applicable | 0 | 2005 | 2005 | 12.8 | 12.8 MW | 48 |  |  | 0 |  | WHI0111 | HBY - Hawkes Bay | NI - North Island | Rated at 12.8MW but actually generating 5.5MW on average |  | EECA |  | No current series | 0
Patea |  | Trustpower | Trustpower | Grid Connected | Hydro | 30.7 | Hydro | 0.16 | Not Applicable | 0 | May 1984 | 1984 | 30.7 | 10 MW | 118 | 3 x 10 MW, 1 x 0.7 MW |  | 0 |  | HWA1101 | TRN - Taranaki | NI - North Island | Patea power station is situated on the Patea River in South Taranaki and takes advantage of the river's good water flows, 871km2 catchment and long deep river gorge. The site was identified in 1974 and the dam was completed in 1983 with the station commissioned in 1984. The dam is 82 metres high and holds back Lake Rotorangi, which at 45 kilometres is New Zealand's longest man made lake. The station has 31 MW generation capacity and has an average annual output of 118 GWh. As there is a significant eel fishery up and down stream of Patea dam, a pass for young eels has been constructed and is maintained by TrustPower. An active trap and transfer programme, partially funded by TrustPower, is also in operation, and gate operations are timed to help downstream migration of mature eels |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Patea | 0
Patearoa | Paerau Gorge Power Scheme | Trustpower | Trustpower | Embedded | Hydro | 2.25 | Hydro | 0 | Not Applicable | 0 | 1984 | 1984 | 2.25 | 2.25 MW | 8 |  |  | 0 |  | NSY0331 | OTG - Otago/Southland | NI - North Island | The combined power and irrigation scheme operates by diverting the Taieri River's flow at Paerau using a substantial weir structure in the river which maintains the water level into the scheme while allowing floods and a minimum river flow to pass. The scheme's inflow passes along an aquaduct through substantial cuttings and a 1.3 kilometre long tunnel before feeding the Paerau Power Station. The outflow from the power station fills a large ponding area from which the irrigation scheme and Patearoa Power Station draw. The irrigation scheme now extends for 35 kilometres down the western side of Maniototo basin. The east side proposal is limited to the second power station near Patearoa which discharges back into the Taieri river. When low flows occur during summer, supplementary flows will be released from the Loganburn Reservoir formed at the site of Great Moss Swamp to ensure minimum river flows are maintained and that sufficient irrigation water is available to the scheme. |  | www.trustpower.co.nz,EMS (Reconciliation Manager List) |  | GEN.Hydro.Paerau | 0
Piriaka |  | King Country Energy | King Country Energy | Embedded | Hydro | 1.8 | Hydro | 0 | Not Applicable | 0 | 1924 | 1924 | 1.8 | 1.2 MW | 7 |  |  | 0 |  | HTI0331 | CEN - Central | NI - North Island | The station was opened in 1924 to supply Taumarunui with electricity. In 1938 an agreement was signed with the Government and the local system was connected to the national electricity system to cope with local load growth. In 1971 an additional hydro generator was added. |  | www.toddenergy.co.nz,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Piriaka | 0
Piripaua | Waikaremoana | Genesis Energy | Genesis Energy | Grid Connected | Hydro | 42 | Hydro | 0.942 | Not Applicable | 0 | 1943 | 1943 | 42 | 21 MW | 133 | 2 x 21 MW |  | 0 |  | TUI1101 | HBY - Hawkes Bay | NI - North Island | Piripaua is the last station of the Waikaremoana system drawing water from Lake Whakamarino before releasing it into the Waikaretaheke River. The Waikaremoana Hydro Scheme is located between the remote Te Urewera National Park and Wairoa. The scheme includes the Kaitawa (36MW), Tuai (60MW)and Piripaua (42MW)hydro stations, and is centrally controlled from Tuai. Water from Lake Waikaremoana flows through the Kaitawa power station and into Lake Kaitawa before reaching the Tuai power station. From there it flows into the man-made Lake Whakamarino and through the Piripaua power station, before being released into the Waikaretaheke River and making its way to the sea. |  | www.genesisenergy.co.nz,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Waikaremoana | 0
Plimmerton |  | Right House | Meridian Energy | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | PNI0331 | WEL - Wellington | NI - North Island |  |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Plimmerton | 0
Poihipi Rd |  | Contact Energy | Contact Energy | Grid Connected | Geothermal | 55 | Geothermal | 0 | Not Applicable | 0 | 1997 | 1997 | 55 | 55 MW | 350 |  |  | 0 |  | PPI2201 | WTO - Waikato | NI - North Island | The Poihipi Road power station was commissioned in 1997 and was bought by Contact in January 2000. It is now operated as an integral part of the Wairakei facility and is supplied with steam from the Wairakei geothermal system. Poihipi currently generates around 200 GWh per year. Poihipi is subject to resource constraints hence the reduced GWh relative to installed MW |  | www.mycontact.co.nz,EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List),www.nzgeothermal.org.nz, ACS data |  | GEN.Geothermal.Poihipi | PPI2201 PPI0
Port Chalmers |  | Port Otago | Meridian Energy | Embedded | Unknown | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0.01 MW | 0 |  |  | 0 |  | HWB0331 | OTG - Otago/Southland | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Dunedin.PortChalmers | 0
PukePine |  | PukePine Sawmills | Trustpower | Embedded | Thermal | 0 | Diesel | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | TMI0331 | BOP - Bay Of Plenty | NI - North Island |  |  | EMS (Reconciliation Manager List),CDS |  | GEN.Thermal.Pukepine | 0
Pupu Hydro |  | Pupu Hydro Society | Contact Energy | Embedded | Hydro | 0.3 | Hydro | 0 | Not Applicable | 0 |  |  | 0.3 | 0.3 MW | 1.7 |  |  | 0 |  | MPI0661 | NEL - Nelson/Marlbourough | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Pupu | 0
Raetihi |  | Trustpower | Trustpower | Embedded | Hydro | 0.3 | Hydro | 0 | Not Applicable | 0 |  |  | 0.3 | 0.3 MW | 1.3 |  |  | 0 |  | OKN0111 | CEN - Central | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Raetihi | 0
Rangipo | Tongariro Power Development | Genesis Energy | Genesis Energy | Grid Connected | Hydro | 120 | Hydro | 0 | Not Applicable | 0 | 1983 | 1983 | 120 | 60 MW | 580 |  |  | 0 |  | RPO2201 | CEN - Central | NI - North Island | The Tongariro Power Scheme gathers water from the mountains of the central volcanic plateau in the North Island. The water passes through two power stations Rangipo (120MW) and Tokaanu (240MW) before being released into Lake Taupo. The scheme taps a catchment area of more than 2600 sq km and uses a series of lakes, canals and tunnels to bring water to the two stations which typically generate 1400 GWh p.a.—about 4% of the country's total electricity generation. The western diversion takes water from six rivers and streams from the Whakapapa River to the Whanganui River, into Lake Rotoaira via Lake Otamangakau. The Tokaanu power station is connected to Lake Rotoaira via a six kilometre tunnel through Mount Tihia. It also draws water from the Tongariro River via the Poutu tunnel and canal. On the eastern side of Mount Ruapehu, water is diverted from the Kaimanawa Ranges and headwaters of the Wahianoa River through a 20 km tunnel into the Rangipo dam. The 120MW Rangipo power station is 230 metres below ground. Its turbines are located in a cavern cut from solid rock and lined with concrete. |  | Electricity Commission,EMS (Reconciliation Manager List), www.genesisenergy.co.nz |  | GEN.Hydro.Rangipo | 0
Ravensbourne |  | Ravensdown Fertiliser Co-op | Meridian Energy | Embedded | Cogeneration | 0.5 | Unknown | 0 | Not Applicable | 0 |  |  | 0.5 | 0.5 MW | 1.1 |  |  | 0 |  | HWB0332 | OTG - Otago/Southland | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Dunedin.Ravensbourne | 0
Ravensdown |  | Vector | Meridian Energy | Embedded | Cogeneration | 8 | Unknown | 0 | Not Applicable | 0 |  |  | 8 | 8 MW | 32 |  |  | 0 |  | RDF0331 | HBY - Hawkes Bay | NI - North Island |  |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.Napier.Awatoto | 0
Redvale Landfill |  | Waste Management | Trustpower | Embedded | Other | 7 | Biogas | 0 | Not Applicable | 0 |  |  | 7 | 1 MW | 50 | 7 x 1 MW |  | 0 |  | SVL0331 | NIS - North Isthmus | NI - North Island |  |  | Electricity Commission,EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Redvale | 0
Roaring Meg |  | Pioneer Generation | Trustpower | Embedded | Hydro | 4.2 | Hydro | 0 | Not Applicable | 0 | 1936 | 1936 | 4.2 | 1.5 MW | 29 |  |  | 0 |  | CML0331 | OTG - Otago/Southland | SI - South Island | The scheme was originally commissioned in 1936 and is made up of an upper and lower station. The intake dam is located 3.6km upstream of the confluence with the Kawarau River. The 10 metre high intake dam feeds a series of pipelines terminating at the stations, which each house two turbines. The lower station discharges directly into the Kawarau River while the upper station discharges both into a pipeline feeding the lower station and the Roaring Meg Stream |  | Electricity Commission,EMS (Reconciliation Manager List),www.qldc.govt.nz, www.centrallakestrust.org.nz |  | GEN.Hydro.RoaringMeg | 0
Rochfort |  | Kawatiri Energy | Kawatiri Energy | Embedded | Hydro | 4.2 | Hydro | 0 | Not Applicable | 0 | Jul 2013 | 2013 | 4.2 | 4.2 MW | 20 | 1 x 4.2 MW |  | 0 |  | ORO1101 | WEC - West Coast | SI - South Island |  |  | www.energynews.co.nz |  | No current series | #N/A
Rosedale Landfill |  | EnviroWaste | Mighty River Power | Embedded | Other | 2.8 | Biogas | 0 | Not Applicable | 0 | 1992 | 1992 | 2.8 | 0.92 MW | 22 | 3 x 0.92 MW |  | 0 |  | ALB0331 | NIS - North Isthmus | NI - North Island |  |  | Electricity Commission,EMS (Reconciliation Manager List),www.entec.co.nz,CDS |  | GEN.Thermal.Auckland.Rosedale | 0
Rotokawa |  | Mighty River Power | Mighty River Power | Embedded | Geothermal | 33 | Geothermal | 0 | Not Applicable | 0 | Sep 1997 | 1997 | 34 | 16 MW | 210 | 1 x 16 MW, 4 x 6.5 MW |  | 0 |  | WRK0331 | WTO - Waikato | NI - North Island | The Rotokawa power station is part of a joint venture between Mighty River Power and Tauhara North No.2 Trust. It includes the generation plant owned by Mighty River Power, and wells that tap the steam field which are owned by Rotokawa Joint Venture Ltd. The nominal capacity of Rotokawa was initially 25MW, but has since been expanded to 34MW. The output of the binary units is highly dependent on ambient air temperature as they use a low boiling point (34C) hydrocarbon heated by exhaust steam to drive the secondary turbines. Units : 1 16MW back pressure steam turbine, 4 6.5MW binary units. |  | EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List),www.mightyriverpower.co.nz |  | GEN.Geothermal.Rotokawa.Wairakei | 0
Roxburgh | Clutha Hydro Scheme | Contact Energy | Contact Energy | Grid Connected | Hydro | 320 | Hydro | 0.388 | Not Applicable | 0 | 1956 | 1956 | 320 | 40 MW | 1610 |  |  | 0 |  | ROX1101 | OTG - Otago/Southland | SI - South Island | Roxburgh injects on 110kv and 220kv buses, ROX1101 and ROX2201, 3 units and 5 units respectively. The first of Roxburgh's eight generators was commissioned in 1956, the last in 1962. The power station has a capacity of 320 megawatts. Roxburgh is a concrete gravity dam, and with the powerhouse, contains about half a million cubic metres of concrete, weighing 1.5 million tonnes. The lake formed by the dam covers an area of nearly six square kilometres |  | www.mycontact.co.nz,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Clutha.Roxburgh.110KV,GEN.Hydro.Clutha.Roxburgh.220KV | 0
Ruahihi | Kaimai Hydro Power Scheme | Trustpower | Trustpower | Embedded | Hydro | 20 | Hydro | 0 | Not Applicable | 0 | 1981 | 1981 | 20 | 10 MW | 76 | 2 x 10 MW |  | 0 |  | TGA0331 | BOP - Bay Of Plenty | NI - North Island | The Ruahihi Power Station is situated on the Wairoa River adjacent to SH29. Ruahihi is the third and largest section of the overall scheme. Construction contracts were let in mid 1977, and the station was commissioned in 1981, but a failure in the feed canal later that year required major rebuilding. The station was recommissioned in 1983. The reservoir for this station is Lake McLaren and the canal links the reservoir to the station. Lake McLaren was formed in 1925 by the construction of a 26m high concrete arch dam across the lower Mangapapa River to operate the now decommissioned McLarens Falls Power Station. Water from the lake passes through a gated inlet structure into a 2.5 kilometre long canal. The construction of the canal involved moving 2, 400, 000 cubic metres of soil at depths up to 46 m below original ground level, making it one of the larger canals in New Zealand. The depth of the water in this canal is 6m and the width at normal operating level is 30m. Flow velocities are up to 0.9m per second depending on machine settings and water levels. Transition from the canal to penstock is a forebay which again has screens, a cleaner and control gates. Downstream of the forebay is a 1.6km low pressure conduit leading to twin high pressure penstock pipes down the escarpment and under State Highway 29 into the power house. |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Kaimai.1 | 0
Silverstream Landfill |  | Mighty River Power | Mighty River Power | Embedded | Other | 2.7 | Biogas | 0 | Not Applicable | 0 | 1994 | 1994 | 2.7 | 0.9 MW | 13 | 3 x 0.9 MW |  | 0 |  | HAY0331 | WEL - Wellington | NI - North Island |  |  | PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List),www.entec.co.nz,CDS |  | GEN.Thermal.Wellington.Silverstream | 0
Simeon Quay |  | Orion | Orion | Embedded | Backup generation | 0.7 | Unknown | 0 | Not Applicable | 0 |  |  | 0.7 | 0.7 MW | 0 |  |  | 0 |  | BRY0111 | CAN - Canterbury | SI - South Island | Negligible GWh |  | Electricity Commission,EMS (Reconciliation Manager List),CDS |  | GEN.Unknown.Christchurch.Bromley.SimeonQuay | 0
South Pacific Cellars |  | South Pacific Cellars | Trustpower | Embedded | Backup generation | 0.2 | Diesel | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0 |  |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island |  |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Blenheim.Riverlands.SouthPacific | 0
Southbridge Wind |  | Energy3 | Meridian Energy | Embedded | Wind | 0.1 | Wind | 0 | Not Applicable | 0 | 2005 | 2005 | 0.1 | 0.1 MW | 0.4 | 1 x 0.1 MW |  | 0 |  | SPN0331 | CAN - Canterbury | SI - South Island |  |  | windenergy.org.nz, EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Leeston | 0
Southdown |  | Mighty River Power | Mighty River Power | Grid Connected | Thermal | 140 | Gas | 8250 | Not Applicable | 0 | Dec 1996 | 1996 | 175 | 45 MW | 400 | 3 x 45 MW , 1 x 35 MW (although total is reported as 175MW) |  | 0 |  | SWN2201 | AKL - Auckland | NI - North Island | The 35MW gas turbine was mothballed end of 2013. MRP have announced that the remaining units will be decommissioned at the end of 2015. | 2015 | EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.Southdown | 0
Southern Landfill |  | Todd Energy | Todd Energy | Embedded | Other | 1.1 | Biogas | 0 | Not Applicable | 0 |  |  | 1.1 | 1.1 MW | 6 |  |  | 0 |  | CPK0331 | WEL - Wellington | NI - North Island | GWh estimated based on capacity factors for other landfill based generation |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Wellington.Owhiro | 0
St Albans, Christchurch |  | Christchurch City Council | Meridian Energy | Embedded | Unknown | 0.2 | Unknown | 0 | Not Applicable | 0 |  |  | 0.2 | 0.2 MW | 0 |  |  | 0 |  | PAP0661 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List) |  | GEN.Unknown.Christchurch.Papanui.StAlbans | 0
Stratford Austral Pacific |  | Austral Pacific Energy | Genesis Energy | Embedded | Unknown | 1 | Unknown | 0 | Not Applicable | 0 |  |  | 1 | 1 MW | 5 |  |  | 0 |  | SFD0331 | TRN - Taranaki | NI - North Island | GWh and MW estimated from Centralised Dataset |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Stratford.Cheal | 0
Stratford Peaker |  | Contact Energy | Contact Energy | Grid Connected | Thermal | 200 | Gas | 0 | Not Applicable | 0 | 2011 | 2011 | 200 | 100 MW | 350 | 2 x 100 MW |  | 0 |  | SFD2201 | TRN - Taranaki | NI - North Island | The two units are high efficiency LMS-100 gas turbine generators. Have assumed 20% utilisation to estimate GWh |  | www.contactenergy.co.nz |  | Gen.Thermal.Stratford | SFD2201 SFD22
Talla Burn |  | Talla Burn Generation | Talla Burn Generation | Embedded | Hydro | 2.6 | Hydro | 0 | Not Applicable |  | 2010 | 2010 | 2.15 | 2.15 MW | 10 |  |  | 0 |  | CYD0331 | OTG - Otago/Southland | SI - South Island | The station is about 30 minutes drive from Roxburgh and operates with a 252-metre gross head and a 1.1 cubic metres per second flow. |  | www.energynews.co.nz |  | No current series | 0
Tararua Stage 1 | Tararua Wind Farm | Trustpower | Trustpower | Embedded | Wind | 31.7 | Wind | 0 | Not Applicable | 0 | Mar 1999 | 1999 | 31.7 | 0.66 MW | 128 | 48 x 0.66 MW |  | 0 |  | LTN0331 | CEN - Central | NI - North Island |  |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Wind.Tararua.Linton | 0
Tararua Stage 2 | Tararua Wind Farm | Trustpower | Trustpower | Embedded | Wind | 36.3 | Wind | 0 | Not Applicable | 0 | May 2004 | 2004 | 36.3 | 0.66 MW | 147 | 55 x 0.66 MW |  | 0 |  | BPE0331 | CEN - Central | NI - North Island |  |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Wind.Tararua.Bunnythorpe | 0
Tararua Stage 3 | Tararua Wind Farm | Trustpower | Trustpower | Grid Connected | Wind | 93 | Wind | 0 | Not Applicable | 0 | 2007 | 2007 | 93 | 3 MW | 375 | 31 x 3 MW |  | 0 |  | TWC2201 | CEN - Central | NI - North Island | Tararua 3 consists of 31 3MW turbines totalling 93 MW. Assuming a similar plant factor as the existing plant gives an approximate yield of 375 Gwh per annum. Construction of Tararua 3 is expected to be completed by July 2007 |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Wind.Tararua.Grid | 0
TCC - Taranaki Combined Cycle |  | Contact Energy | Contact Energy | Grid Connected | Thermal | 385 | Gas | 7600 | Not Applicable | 0 | Jul 1998 | 1998 | 385 | 385 MW | 2200 |  |  | 0 |  | SFD2201 | TRN - Taranaki | NI - North Island | Taranaki Combined Cycle was the first large-scale combined cycle gas turbine station to be built in New Zealand. Construction began in July 1996, with the plant completed in July 1998. The 367 megawatt station uses approximately 1.4 million cubic metres of natural gas per day in generation, and has an efficiency of around 55.5%. Capacity at the plant was increased from 367 to 385 MW during refurbishment in 2008. |  | www.mycontact.co.nz,EL DatabasePB 'Thermal & Geothermal Generation Capabilities',,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.Stratford.B | SFD2201 SPL0
Te Apiti |  | Meridian Energy | Meridian Energy | Grid Connected | Wind | 90.75 | Wind | 0 | Not Applicable | 0 | Nov 2004 | 2004 | 90.75 | 1.65 MW | 258 | 55 x 1.65 MW |  | 0 |  | WDV1101 | CEN - Central | NI - North Island |  |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Wind.Tararua.TeApiti | 0
Te Awamutu - Anchor Products |  | Genesis Energy | Genesis Energy | Grid Connected Cogen | Cogeneration | 0 | Gas | 13800 | Not Applicable | 0 | 1995 | 1995 | 54 | 54 MW | 0 |  |  | 0 |  | TMU1101 | WTO - Waikato | NI - North Island | The generation plant was decommissioned in November 2007. The plant was based on a 54MW Pratt and Whitney aero-derivative Twinpak gas turbine exhausting into a heat recovery boiler to raise steam for process use. In normal operation only one of the two gas turbines of the Twinpak was in service, with the other available for backup in the case of an outage of the operating unit, or for operation as a peaking unit. | 2007 | EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.TeAwamutu | 0
Te Huka |  | Contact Energy | Contact Energy | Embedded | Geothermal | 23 | Geothermal | 0 | Not Applicable | 0 | 2010 | 2010 | 23 | 23 MW | 190 |  |  | 0 |  | WRK0331 | WTO - Waikato | NI - North Island | A.K.A. Tauhara 1 and Centennial Drive |  | www.contactenergy.co.nz |  | GEN.Geothermal.Tauhara.TeHuka | 0
Te Mihi |  | Contact Energy | Contact Energy | Grid Connected | Geothermal | 166 | Geothermal | 0 | Not Applicable | 0 | 2014 | 2014 | 166 | 83 MW | 1300 | 2 x 83 MW |  | 0 |  | THI2201 | WTO - Waikato | NI - North Island | As at April 2014 TeMihi was still undergoing commissioing testing. The full plant is expecting to be running by July 2014, although some issues were struck with the hot well pumps vibrating when in use that may limit capacity until the problem can be remedied. |  | www.contactenergy.co.nz |  | No current series | #N/A
Te Rapa |  | Contact Energy | Contact Energy | Partially Embedded | Cogeneration | 44 | Gas | 12600 | Not Applicable | 0 | 1999 | 1999 | 44 | 44 MW | 200 |  |  | 0 |  | TWH0331 | WTO - Waikato | NI - North Island | The Te Rapa power station was commissioned in 1999 and is a cogeneration facility providing high quality steam and electricity to Fonterra's Te Rapa factory, one of the world's largest milk powder drying plants. Surplus electricity is directed back to the local area. |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.TeRapa | TWH0331 TRC1
Te Rere Hau |  | New Zealand Wind Farms | New Zealand Wind Farms | Partially Embedded | Wind | 48.5 | Wind | 0 | Not Applicable | 0 | 2011 | 2011 | 48.5 | 0.5 MW | 160 | 97 x 0.5 MW |  | 0 |  | TWC2201 | CEN - Central | NI - North Island | The windfarm was built in separate stages between 2006 and 2011. While all 5 stages are technically embedded behind Tararua C, their output is mainly injected onto the grid. Stage 1 (5 turbines) was completed in September 2006 and was initially embedded fully in the local lines network. Stage 2 (28 turbines) was completed in April 2009, at which point a notionally-embedded connection to the grid was installed. Stage 3 (32 turbines) was completed in November 2009. Stages 4 and 5 (32 turbines) were completed in July 2011. |  | EMS (Reconciliation Manager List), CDS,www.nzwindfarms.co.nz |  | GEN.Wind.Tararua.TeRereHau.Linton, GEN.Wind.Tararua.TeRereHau.Grid | 0
Te Uku |  | WEL Networks / Meridian Energy | Meridian Energy | Embedded | Wind | 64.4 | Wind | 0 | Not Applicable | 0 | 2011 | 2011 | 64.4 | 2.3 MW | 225 | 28 x 2.3 MW |  | 0 |  | TWH0331 | WTO - Waikato | NI - North Island | Joint partnership between WEL and Meridian |  | www.meridianenergy.co.nz |  | GEN.Wind.TeUku | 0
Tekapo A | Waitaki Hydro Scheme | Genesis Energy | Genesis Energy | Grid Connected | Hydro | 25 | Hydro | 0.232 | Not Applicable | 0 | 1951 | 1951 | 25 | 25 MW | 160 |  |  | 0 |  | TKA0111 | SCN - South Canterbury | SI - South Island | The Tekapo A station flows are supplied by a 1.6 km tunnel from the Lake Tekapo intake. The flow of water is controlled by a dam at Tekapo that can store flood waters or spill excess capacity into the Tekapo River. Water that passes through Tekapo A continues down a canal to the Tekapo B station situated on Lake Pukaki. Water spilled into the Tekapo River can be diverted into the Tekapo canal and onto Tekapo B or allowed to flow down the river to Lake Benmore. |  | www.meridianenergy.co.nz,Electricity Commission,EMS (Reconciliation Manager List), www.genesisenergy.co.nz | 1 | GEN.Hydro.Waitaki.Tekapo | 0
Tekapo B | Waitaki Hydro Scheme | Genesis Energy | Genesis Energy | Grid Connected | Hydro | 160 | Hydro | 1.282 | Not Applicable | 0 | 1977 | 1977 | 160 | 80 MW | 800 |  |  | 0 |  | TKB2201 | SCN - South Canterbury | SI - South Island | Located at end of a 26.5 kilometre-long canal which takes water from Tekapo A; average canal depth, 5.3 metres. There is a 147 metre height difference between the canal and Lake Pukaki. Constructed in 1977 on dry land but was surrounded by water when Lake Pukaki was raised to a new range of operating levels following the completion of the Pukaki high dam. Substructure is 32 metres high on top of which is the (visible) station superstructure. |  | www.meridianenergy.co.nz,Electricity Commission,EMS (Reconciliation Manager List) | 2 | GEN.Hydro.Waitaki.Pukaki | 0
Templeton |  | Department of Corrections | Meridian Energy | Embedded | Thermal | 0.1 | Unknown | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0 |  |  | 0 |  | ISL0331 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Christchurch.Islington.Templeton | 0
Teviot | Teviot Hydro Scheme | Pioneer Generation | Trustpower | Partially Embedded | Hydro | 10.5 | Hydro | 0 | Not Applicable | 0 | 1983 | 1983 | 10.5 | 6.8 MW | 55 | 1 x 6.8 MW, 1 x 1.125 MW, 1 x 1 MW, 1 x 1.6 MW |  | 0 |  | CYD0331 | OTG - Otago/Southland | SI - South Island | Teviot 55 GWh from Pioneer Generation fact sheet published on Central Lakes Trust website based on Teviot total scheme 78 Gwh, with 55 GWh under Teviot and the remaining 23 GWh under Horseshoe Bend based on MW capacity. Capacity: Ellis 6.8MW, Teviot Bridge 1.125MW, George Station 1 MW, Michelle Station 1.6MW |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List),www.centrallakestrust.org.nz | 2 | GEN.Hydro.Teviot | 0
Tirohia Landfill |  | H.G. Leach & Co. | Mighty River Power | Embedded | Other | 1 | Biogas | 0 | Not Applicable | 0 | 2008 | 2008 | 1 | 1 MW | 7.5 | 1 x 1 |  | 0 |  | WKO0331 | WTO - Waikato | NI - North Island | The landfill gas engine is a Waukesha APG1000 48 liitre V16 operating at 1500RPM. |  | www.hgleach.co.nz |  | No current series | 0
Tokaanu | Tongariro Power Development | Genesis Energy | Genesis Energy | Grid Connected | Hydro | 240 | Hydro | 1.754 | Not Applicable | 0 | 1973 | 1973 | 240 | 60 MW | 763 |  |  | 0 |  | TKU0331 | CEN - Central | NI - North Island | The Tongariro Power Scheme gathers water from the mountains of the central volcanic plateau in the North Island. The water passes through two power stations Rangipo (120MW) and Tokaanu (240MW) before being released into Lake Taupo. The scheme taps a catchment area of more than 2600 sq km and uses a series of lakes, canals and tunnels to bring water to the two stations which typically generate 1400 GWh p.a.—about 4% of the country's total electricity generation. The western diversion takes water from six rivers and streams from the Whakapapa River to the Whanganui River, into Lake Rotoaira via Lake Otamangakau. The Tokaanu power station is connected to Lake Rotoaira via a six kilometre tunnel through Mount Tihia. It also draws water from the Tongariro River via the Poutu tunnel and canal. On the eastern side of Mount Ruapehu, water is diverted from the Kaimanawa Ranges and headwaters of the Wahianoa River through a 20 km tunnel into the Rangipo dam. The 120MW Rangipo power station is 230 metres below ground. Its turbines are located in a cavern cut from solid rock and lined with concrete. |  | Electricity Commission,EMS (Reconciliation Manager List), www.genesisenergy.co.nz |  | GEN.Hydro.Tokaanu | 0
Totara Road |  | Palmerston North City Council | Mighty River Power | Embedded | Thermal | 0.8 | Unknown | 0 | Not Applicable | 0 |  |  | 0.8 | 0.8 MW | 2.3 |  |  | 0 |  | LTN0331 | CEN - Central | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.PalmerstonNorth.Awapuni | 0
Tuai | Waikaremoana | Genesis Energy | Genesis Energy | Grid Connected | Hydro | 60 | Hydro | 1.587 | Not Applicable | 0 | 1929 | 1929 | 60 | 20 MW | 218 | 3 x 20 MW |  | 0 |  | TUI1101 | HBY - Hawkes Bay | NI - North Island | The Tuai station draws water from the Lake Kaitawa and discharges into the man made Lake Whakamarino. The Waikaremoana Hydro Scheme is located between the remote Te Urewera National Park and Wairoa. The scheme includes the Kaitawa (36MW), Tuai (60MW) and Piripaua (42MW) hydro stations, and is centrally controlled from Tuai. Water from Lake Waikaremoana flows through the Kaitawa power station and into Lake Kaitawa before reaching the Tuai power station. From there it flows into the man-made Lake Whakamarino and through the Piripaua power station, before being released into the Waikaretaheke River and making its way to the sea. |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Waikaremoana | 0
Turitea Hydro |  | Palmerston North City Council | Mighty River Power | Embedded | Hydro | 0.1 | Hydro | 0 | Not Applicable | 0 |  |  | 0.1 | 0.1 MW | 0.5 |  |  | 0 |  | LTN0331 | CEN - Central | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.PalmerstonNorth.Turitea.Linton | 0
Wahapo (Okarito Forks) |  | Trustpower | Trustpower | Partially Embedded | Hydro | 3.1 | Hydro | 0 | Not Applicable | 0 | 1960 | 1960 | 3.1 | 3.1 MW | 14.5 |  |  | 0 |  | HKK0661 | WEC - West Coast | SI - South Island | The Wahapo Power Station, formerly known as the Okarito Forks Power Station, had its beginnings at a public meeting in June 1957, and was commissioned, using a generator set of 250 kw that had been employed at the Homer Tunnel project, in 1960. In late 1991 a new station was comissioned using the natural storage of Lake Wahapo, the station has a rated output of 3,100kw and an average annual output of 14.5Gwh |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Hokitika.Wahapo | 0
Waihi Station |  | Trustpower | Trustpower | Embedded | Hydro | 4.7 | Hydro | 0 | Not Applicable | 0 | 1913 | 1913 | 4.7 | 2.35 MW | 10.4 | 2 x 2.35 MW |  | 0 |  | WRA0111 | HBY - Hawkes Bay | NI - North Island |  |  | Electricity Commission,EMS (Reconciliation Manager List),www.waihi.co.nz |  | GEN.Hydro.Waihi | 0
Waihopai |  | Trustpower | Trustpower | Embedded | Hydro | 2.5 | Hydro | 0 | Not Applicable | 0 | Aug 1927 | 1927 | 2.5 | 2 MW | 11.8 |  |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island | Originally of 1,000 kW capacity, and intended to supply the entire Marlborough province, the Waihopai scheme was expanded to meet growing demand for electricity thorugh the installation of diesel generating sets in 1930 and 1937. Plans to increase capacity during 1943 were blocked due to Government wartime import restrictions. In 1996 a new 2,000 kw generator and turbine were installed to supplement one of the existing 500 kW units. This and other upgrade work has seen the scheme's maximum output increase from 1,000kw to 2,500 kW, with an annual generation output of 11.8 GWh. |  | www.trustpower.co.nz,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Waihopai | 0
Waipapa | Waikato Hydro Scheme | Mighty River Power | Mighty River Power | Grid Connected | Hydro | 51 | Hydro | 0.143 | Not Applicable | 0 | Nov 1961 | 1961 | 51 | 17 MW | 242 | 3 x 17 MW |  | 0 |  | WPA2201 | WTO - Waikato | NI - North Island | As the smallest power station in the Waikato River hydro system, the role of Waipapa is to supplement the other stations during periods of heavy demand. At these times, the lake level fluctuates over a wide range. On other occasions, Waipapa is required to spill water past the station to accommodate upstream and downstream generation requirements. The volume of water flowing from the Maraetai station upstream, as well as the small reservoir size can create a 'bottleneck' in the Waikato hydro system. Capacity is normally 51MW, although under favourable hydrology conditions this may rise as high as 58.7MW (MRP website). |  | Electricity Commission,EMS (Reconciliation Manager List) | 6 | GEN.Hydro.Waikato.Waipapa | 0
Waipori |  | Trustpower | Trustpower | Combination, Grid Connected/Embedded | Hydro | 84 | Hydro | 0.36 | Not Applicable | 0 | 1902 | 1902 | 84 | 19 MW | 178 |  |  | 0 |  | BWK1101 | OTG - Otago/Southland | SI - South Island | The scheme's development was commenced in 1902 by the Waipori Falls Electric Power Company, which in 1904 was purchased by Dunedin City Council. The first electricity generation occurred in 1907 and development of the hydro capacity of the Waipori River has been ongoing ever since. In 1998 TrustPower acquired the scheme from Dunedin City Council for $70 million. The Waipori hydro scheme is some 30 kilometres inland from Dunedin in the Lammerlaw Range. It comprises four individual dams and power stations that act in sequence with the powerhouses delivering output of 12 MW, 57 MW, 7 MW and 8 MW respectively as water descends down the Waipori River. The scheme is partially grid connected and partially embedded within the local line network. One of the units on the 2A station is switchable between the 33kv system (embedded) and the 110 kv system (31 MW is embedded, 34 MW is grid connected and 19MW can be switched betwen either). Grid connection bus is BWK1101 TRUS GG. Embedded bus is behind HWB0331. CDS output data is believed to be net of some local load. |  | www.trustpower.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | SI.Dunedin.HalfwayBush.Local, SI.Berwick.Import | 0
Wairakei |  | Contact Energy | Contact Energy | Grid Connected | Geothermal | 161 | Geothermal | 0 | Not Applicable | 0 | Nov 1958 | 1958 | 175 | 30 MW | 1310 | 6 x 11.2 MW, 3 x 30 MW, 1 x 4 MW, 1 x 14 MW |  | 0 |  | WRK2201 | WTO - Waikato | NI - North Island | The Wairakei power plant is situated above a large geothermal system containing water at temperatures up to 240°C. Currently, about 5,000 tonnes per hour of fluid is taken from the reservoir. This is separated into roughly 1,500 tonnes per hour of steam and 3,500 tonnes per hour of water at a temperature of about 130°C. Dry steam is also taken from shallow production wells (up to 500 m depth) and piped directly to the turbines. The steam is directed towards the turbines through the network of pipes around the Wairakei steam field. Once steam has passed through the turbines it is condensed within 'direct contact' condensers. This cooling system uses water pumped from the adjacent Waikato River. After use, the cooling water and steam condensate is discharged back into the river. Gases found in the steam supply are pumped from the condenser and released to the air via gas stacks situated on the power station roof. The hot geothermal water is discharged into a system of drains (that lead to the Waikato River), or it is injected back into the ground. The Binary Plant uses heat energy in waste hot water to drive two 8 MW generators. However the binary plant needs about 2MW of power just to run its own pumps and fans so the overall generation is 14MW |  | EL Database,PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List),www.nzgeothermal.org.nz |  | GEN.Geothermal.Wairakei | WRK2201 WRK0
Wairau | Branch Hydro Scheme | Trustpower | Trustpower | Grid Connected | Hydro | 7.2 | Hydro | 0 | Not Applicable | 0 | May 1983 | 1983 | 7.2 | 7.2 MW | 31 |  |  | 0 |  | ARG1101 | NEL - Nelson/Marlbourough | SI - South Island | Investigations into the feasibility of Branch River Power scheme began in 1978, and following a detailed investigation in 1980 finance was approved with construction beginning soon afterwards. Canal filling commenced in March 1983, with generation commencing at the Wairau Power House in June, and at Argyle two months later. A run of the river scheme with daily storage, the water first passes through the Argyle station of 3800kw capacity with a head of 21.9 meters. A 3385 meter canal then carries the water to the Wairau Power Station of 7200kw at a head of 41.3 metres. CDS output data is believed to be net of some local load. |  | www.trustpower.co.nz,Electricity Commission,EMS (Reconciliation Manager List) | 2 | SI.Argyle.Import | 0
Wairere Falls |  | King Country Energy | King Country Energy | Embedded | Hydro | 4.9 | Hydro | 0 | Not Applicable | 0 | 1963 | 1963 | 4.9 | 3.3 MW | 18 |  |  | 0 |  | ONG0331 | CEN - Central | NI - North Island | The Mokau River has a catchment area of 580 square kilometers, dammed by a concrete dam rising 3.5 meters in height above the top of the falls. The original power station was commissioned in 1925 beside the Wairere Falls (turbine 1) with just one machine giving an output of 490 kilowatts. Later three more machines were added in 1938 (turbine 2), 1952 (turbine 3) and 1981 (turbine 4) with associated penstocks, buildings and tailraces. |  | www.toddenergy.co.nz,Electricity Commission,EMS (Reconciliation Manager List), ACS data |  | GEN.Hydro.Wairere | 0
Wairoa |  | Eastland Networks | Contact Energy | Embedded | Unknown | 0.8 | Unknown | 0 | Not Applicable | 0 |  |  | 0.8 | 0.8 MW | 0.2 |  |  | 0 |  | WRA0111 | HBY - Hawkes Bay | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Unknown.Wairoa | 0
Wairua Falls |  | Northpower | Meridian Energy | Embedded | Hydro | 5 | Hydro | 0 | Not Applicable | 0 | 1978 | 1978 | 5 | 3 MW | 22 |  |  | 0 |  | MPE0331 | NIS - North Isthmus | NI - North Island | The station was upgraded from 3.6MW to 5MW in 2007. A 5 MW generator would give approximately 22 GWh p.a. (50% plant factor). |  | Electricity Commission,EMS (Reconciliation Manager List),www.northpower.com |  | GEN.Hydro.Wairua | 0
Waitaki | Waitaki Hydro Scheme | Meridian Energy | Meridian Energy | Grid Connected | Hydro | 90 | Hydro | 0.162 | Not Applicable | 0 | 1935 | 1935 | 105 | 15 MW | 500 | 7 x 15 MW |  | 12 |  | WTK0111 | OTG - Otago/Southland | SI - South Island | It was constructed in two parts, starting with a cofferdam (a temporary dam used to hold water during construction) to divert water to the Otago (south) side of the river. The other part was built on the Canterbury (north) side of the river, with 11 sluice gates enabling water to flow through while the second section was being built on the Otago side. The station’s powerhouse was completed in 1934 after the dam was built. It was made of reinforced concrete and was 109 metres long. It was extended to 152 metres in the early 1950s to house the last set of new generators. The station’s first two generators were commissioned in 1935, and a third generator in 1940. Two more generators were installed in 1941 and 1949, bringing the station to its capacity of 75 MW. In 1952 the Pukaki and Tekapo water storage projects were finished, and the power station took advantage of the improved water flow. The station’s sixth and seventh generators – each 15 MW – were installed in 1954, and the station increased its capacity to the present-day level of 105 MW. 'The Waitaki is the last station of the system and must be operated to maintain the minimum flow requirements under the Waitaki Water Allocation Rules. In 2011 one of the units (Unit 3) was mothballed, bringing the operating capacity back down to 90 MW. |  | www.meridianenergy.co.nz,EL Database,Electricity Commission,EMS (Reconciliation Manager List) | 8 | GEN.Hydro.Waitaki.Waitaki | 0
Watercare Clevedon |  | Watercare Services | Meridian Energy | Embedded | Thermal | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | TAK0331 | AKL - Auckland | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Ardmore | 0
Watercare Cossey's Dam |  | Counties Power | Mighty River Power | Embedded | Hydro | 0 | Hydro | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | BOB0331 | AKL - Auckland | NI - North Island |  |  | EMS (Reconciliation Manager List) |  | GEN.Hydro.Auckland.Cossey | 0
Watercare Mangere |  | Watercare Services | Mighty River Power | Embedded | Cogeneration | 7 | Biogas | 0 | Not Applicable | 0 | Apr 2003 | 2003 | 7 | 7 MW | 0.1 |  |  | 0 |  | MNG0331 | AKL - Auckland | NI - North Island | Total annual injection into local network less than 0.1 GWh for 2006/07 in CDS |  | EMS (Reconciliation Manager List),CDS |  | GEN.Thermal.Mangere.Watercare | 0
Watercare Wairoa Dam |  | Counties Power | Mighty River Power | Embedded | Hydro | 0 | Hydro | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | BOB0331 | AKL - Auckland | NI - North Island |  |  | EMS (Reconciliation Manager List) |  | GEN.Hydro.Auckland.Wairoa | 0
Watercare Waitakere |  | United Networks | Mighty River Power | Embedded | Hydro | 0 | Hydro | 0 | Not Applicable | 0 |  |  | 0 | 0.03 MW | 0.1 |  |  | 0 |  | HEN0331 | NIS - North Isthmus | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Hydro.Auckland.Waitakere | 0
Weld Cone Wind |  | Energy3 | Meridian Energy | Embedded | Wind | 0.75 | Wind | 0 | Not Applicable | 0 | 2010 | 2010 | 0.75 | 0.25 MW | 3 | 3 x 0.25 MW |  | 0 |  | BLN0331 | NEL - Nelson/Marlbourough | SI - South Island | The wind farm's three turbines are secondhand Micon 530 wind turbines, each with a capacity of 250kW. They were brought in from Germany and Denmark and refurbished in Christchurch. |  | windenergy.org.nz |  | No current series | 0
Wellington Hospital |  | Vector | Meridian Energy | Embedded | Cogeneration | 8 | Gas | 0 | Fuel_Oil | 0 | 1981 | 1981 | 10 | 2 MW | 0 |  |  | 0 |  | CPK0331 | WEL - Wellington | NI - North Island | Total annual injection into local network less than 0.1GWh per annum from CDS. Primarily used for backup. Consumption mainly internal to hospital when running. 4x Merriless-Blackstone 8cyl recip diesels with Brush Alternators 2.5MW rated, 2.0MW MCR |  | EMS (Reconciliation Manager List),CDS, ACS |  | GEN.Thermal.Wellington.Hospital | 0
Wellington Wind Turbine |  | Meridian Energy | Meridian Energy | Embedded | Wind | 0.2 | Wind | 0 | Not Applicable | 0 | 1993 | 1993 | 0.2 | 0.2 MW | 0.8 |  |  | 0 |  | CPK0331 | WEL - Wellington | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Wind.Wellington.Brooklyn | 0
West Wind |  | Meridian Energy | Meridian Energy | Grid Connected | Wind | 143 | Wind | 0 | Not Applicable | 0 | Oct 2009 | 2009 | 143 | 2.3 MW | 550 | 62 x 2.3 MW |  | 0 |  | WWD1102, WWD1103 | WEL - Wellington | NI - North Island |  |  | www.meridianenergy.co.nz |  | GEN.Wind.Makara.Line2, GEN.Wind.Makara.Line3 | 0
Whakamaru | Waikato Hydro Scheme | Mighty River Power | Mighty River Power | Grid Connected | Hydro | 100 | Hydro | 0.315 | Not Applicable | 0 | Dec 1956 | 1956 | 100 | 25 MW | 494 |  |  | 11 |  | WKM2201 | WTO - Waikato | NI - North Island | The Whakamaru power station plays a pivotal role in the Waikato River hydro system. As well as being a significant contributor of electricity to the national grid, its main switching station receives generated power from all the upper Waikato stations, supplying the transmission system that leads north to Otahuhu and South to Bunnythorpe and Haywards. |  | Electricity Commission,EMS (Reconciliation Manager List) | 4 | GEN.Hydro.Waikato.Whakamaru | 0
Whangarei |  | Northland District Health Board | Meridian Energy | Embedded | Thermal | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0 MW | 0 |  |  | 0 |  | MPE0331 | NIS - North Isthmus | NI - North Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Whangarei.Hospital | 0
Wheao and Flaxy Scheme |  | Trustpower | Trustpower | Grid Connected | Hydro | 24 | Hydro | 0.16 | Not Applicable | 0 | 1982 | 1982 | 24 | 12 MW | 115 | 2 x 12 MW |  | 0 |  | ROT0111 | BOP - Bay Of Plenty | NI - North Island | The Wheao and Flaxy scheme had it's beginnings in 1974, with the scheme being commissioned in 1980. The Wheao Hydro Electric Scheme, in the Kaingaroa forest is 82km from Rotorua, 25km from Murupara and 74km from Taupo. The 26MW scheme produces power using water from the Wheao and Rangitaiki Rivers as well as from Flaxy creek. Water from the the Rangitaiki River flows along a 4.7 kilometre open canal into the Wheao penstock intake. When a lot of power is needed the Flaxy Power Station supplements supply. A complex arrangement of canals, tunnels and pipelines feed the water from the upper Wheao River and Flaxy Creek to the Flaxy Power station. |  | www.trustpower.co.nz,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.Wheao | 0
Whirinaki |  | Contact Energy | Contact Energy | Grid Connected | Thermal | 155 | Diesel | 11000 | Not Applicable | 0 | Jun 2004 | 2004 | 155 | 52 MW | 9 |  |  | 0 |  | WHI2201 | HBY - Hawkes Bay | NI - North Island |  |  | EL Database,Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Thermal.Whirinaki | 0
Whisper Tech |  | Whisper Tech | Meridian Energy | Embedded | Thermal | 0 | Unknown | 0 | Not Applicable | 0 |  |  | 0 | 0.002 MW | 0 |  |  | 0 |  | SBK0331 | CAN - Canterbury | SI - South Island | GWh and MW data from Centralised Dataset 2006 calendar year |  | EMS (Reconciliation Manager List), CDS |  | GEN.Thermal.Rangiora | 0
White Hill |  | Meridian Energy | Meridian Energy | Embedded | Wind | 58 | Wind | 0 | Not Applicable | 0 | Jun 2007 | 2007 | 58 | 2 MW | 200 | 29 x 2 MW |  | 0 |  | NMA0331 | OTG - Otago/Southland | SI - South Island | Estimated GWh assumes 40% load factor |  | www.meridianenergy.co.nz |  | GEN.Wind.WhiteHill | 0
Whitford Landfill |  | Waste Management | Trustpower | Embedded | Other | 3 | Biogas | 0 | Not Applicable | 0 |  |  | 3 | 1 MW | 20 | 3 x 1 MW |  | 0 |  | TAK0331 | AKL - Auckland | NI - North Island |  |  | PB 'Thermal & Geothermal Generation Capabilities',Electricity Commission,EMS (Reconciliation Manager List),www.wastemanagement.co.nz,CDS |  | GEN.Thermal.Auckland.Whitford | 0
Wye Creek |  | Pioneer Generation | Trustpower | Embedded | Hydro | 0 | Hydro | 0 | Not Applicable | 0 | 1936 | 1936 | 1.35 | 1.35 MW | 0 |  |  | 0 |  | FKN0331 | OTG - Otago/Southland | SI - South Island | Wye Creek was shut down in 2008 after a pressure build up caused the generator to hurle through a wall into the creek. The scheme is run of the river. Water is collected from small intakes on the north and south branches of Wye Creek which fee 1350m of pipeline varying from 450mm to 600mm in diameter, which in turn supply a small power house downstream of the State Highway 6 road bridge. The scheme was upgraded in 1991 with the addition of a generator, turbine, renewal of penstocks, and foundations and exterior cladding of the powerhouse. The Wye Creek scheme has a peak generation output of 1.35 megawatts and an average energy production 10 Gigawatt hours. |  | Electricity Commission,EMS (Reconciliation Manager List) |  | GEN.Hydro.WyeCreek | 0

## POC analysis
Station_Name | GroupName | Owner_Name | Connection_Type | Generation_Type | Fuel_Name | Node_Name | POC
Opuha |  | Alpine Energy | Partially Embedded | Hydro | Hydro | ABY0111
Addington |  | Orion | Embedded | Unknown | Unknown | ADD0111
Orion Diesel |  | Orion | Embedded | Thermal | Diesel | ADD0661
Orion Diesel II |  | Orion | Embedded | Thermal | Diesel | ADD0661
Christchurch Hospital Campus |  | Christchurch District Health | Embedded | Backup generation | Unknown | ADD0661
Crowne Plaza |  | Crowne Plaza | Embedded | Unknown | Unknown | ADD0661
Rosedale Landfill |  | EnviroWaste | Embedded | Other | Biogas | ALB0331
Aratiatia | Waikato Hydro Scheme | Mighty River Power | Grid Connected | Hydro | Hydro | ARA2201
Argyle | Branch Hydro Scheme | Trustpower | Grid Connected | Hydro | Hydro | ARG1101
Wairau | Branch Hydro Scheme | Trustpower | Grid Connected | Hydro | Hydro | ARG1101
Arapuni | Waikato Hydro Scheme | Mighty River Power | Grid Connected | Hydro | Hydro | ARI1101
Montalto | Rangitata Diversion Race | Trustpower | Partially Embedded | Hydro | Hydro | ASB0331
Cleardale |  | MainPower | Embedded | Hydro | Hydro | ASB0661
Highbank | Rangitata Diversion Race | Trustpower | Partially Embedded | Hydro | Hydro | ASB0661
Atiamuri | Waikato Hydro Scheme | Mighty River Power | Grid Connected | Hydro | Hydro | ATI2201
Aviemore | Waitaki Hydro Scheme | Meridian Energy | Grid Connected | Hydro | Hydro | AVI2201
Milburn |  | Department of Corrections | Embedded | Thermal | Unknown | BAL0331
Mount Stuart |  | Pioneer Generation | Embedded | Wind | Wind | BAL0331
Benmore | Waitaki Hydro Scheme | Meridian Energy | Grid Connected | Hydro | Hydro | BEN0161
Government Communications Satellite |  | Government Communications Satellite | Embedded | Backup generation | Diesel | BLN0331
Indevin |  | Indevin | Embedded | Backup generation | Diesel | BLN0331
Jackson Estate |  | Jackson Estate | Embedded | Backup generation | Diesel | BLN0331
Marlborough Lines Diesel |  | Marlborough Lines | Embedded | Thermal | Diesel | BLN0331
Mud House |  | Kiwi Wine Company | Embedded | Backup generation | Diesel | BLN0331
South Pacific Cellars |  | South Pacific Cellars | Embedded | Backup generation | Diesel | BLN0331
Waihopai |  | Trustpower | Embedded | Hydro | Hydro | BLN0331
Cloudy Bay |  | Indevin | Embedded | Unknown | Unknown | BLN0331
Lulworth Wind |  | Energy3 | Embedded | Wind | Wind | BLN0331
Weld Cone Wind |  | Energy3 | Embedded | Wind | Wind | BLN0331
Marlborough Lines Diesel II |  | Marlborough Lines | Embedded | Thermal | Diesel | BLN0332
Mangatangi Dam |  | Watercare Services | Partially Embedded | Hydro | Hydro | BOB0331
Mangatawhiri |  | Counties Power | Embedded | Hydro | Hydro | BOB0331
Watercare Cossey's Dam |  | Counties Power | Embedded | Hydro | Hydro | BOB0331
Watercare Wairoa Dam |  | Counties Power | Embedded | Hydro | Hydro | BOB0331
Bombay |  | Greymouth Power Company | Embedded | Unknown | Unknown | BOB1101
Palmerston Nth Mini Hydro |  | Palmerston North City Council | Embedded | Hydro | Hydro | BPE0331
Tararua Stage 2 | Tararua Wind Farm | Trustpower | Embedded | Wind | Wind | BPE0331
Marsden Diesel |  | Trustpower | Embedded | Thermal | Diesel | BRB0331
Christchurch City Wastewater |  | Orion | Embedded | Other | Biogas | BRY0111
Aluminium Diecasting Ltd |  | Aluminium Diecasting | Embedded | Unknown | Unknown | BRY0111
Simeon Quay |  | Orion | Embedded | Backup generation | Unknown | BRY0111
Burwood Hospital |  | Christchurch District Health | Embedded | Unknown | Unknown | BRY0661
Waipori |  | Trustpower | Combination, Grid Connected/Embedded | Hydro | Hydro | BWK1101
Roaring Meg |  | Pioneer Generation | Embedded | Hydro | Hydro | CML0331
Cobb |  | Trustpower | Grid Connected | Hydro | Hydro | COB0661
Coleridge |  | Trustpower | Grid Connected | Hydro | Hydro | COL0661
Southern Landfill |  | Todd Energy | Embedded | Other | Biogas | CPK0331
Wellington Hospital |  | Vector | Embedded | Cogeneration | Gas | CPK0331
Wellington Wind Turbine |  | Meridian Energy | Embedded | Wind | Wind | CPK0331
Mangorei |  | Trustpower | Embedded | Hydro | Hydro | CST0331
Fraser |  | Pioneer Generation | Embedded | Hydro | Hydro | CYD0331
Horseshoe Bend | Teviot Hydro Scheme | Pioneer Generation | Partially Embedded | Hydro | Hydro | CYD0331
Kowhai | Teviot Hydro Scheme | Pioneer Generation | Partially Embedded | Hydro | Hydro | CYD0331
Talla Burn |  | Talla Burn Generation | Embedded | Hydro | Hydro | CYD0331
Teviot | Teviot Hydro Scheme | Pioneer Generation | Partially Embedded | Hydro | Hydro | CYD0331
Horseshoe Bend Wind |  | Pioneer Generation | Embedded | Wind | Wind | CYD0331
Clyde | Clutha Hydro Scheme | Contact Energy | Grid Connected | Hydro | Hydro | CYD2201
Arnold |  | Trustpower | Embedded | Hydro | Hydro | DOB0331
Ngahere |  | Birchfield Minerals | Embedded | Hydro | Hydro | DOB0331
Bay Milk Edgecumbe |  | Bay of Plenty Energy | Embedded | Cogeneration | Gas | EDG0331
Oxburn/Glenorchy |  | Pioneer Generation | Embedded | Hydro | Hydro | FKN0331
Wye Creek |  | Pioneer Generation | Embedded | Hydro | Hydro | FKN0331
Matawai |  | Clearwater Hydro | Embedded | Hydro | Hydro | GIS0501
Gisborne |  | Eastland Networks | Embedded | Unknown | Unknown | GIS0501
Glenbrook |  | Alinta Energy | Grid Connected Cogen | Cogeneration | Gas | GLN0332 | GLN0332 GLN0
Mataura |  | Niblick Trust | Embedded | Hydro | Hydro | GOR0331
Blue Mountain Lumber |  | Blue Mountain Lumber | Embedded | Cogeneration | Wood_waste | GOR0331
Hau Nui |  | Genesis Energy | Embedded | Wind | Wind | GYT0331
Silverstream Landfill |  | Mighty River Power | Embedded | Other | Biogas | HAY0331
Watercare Waitakere |  | United Networks | Embedded | Hydro | Hydro | HEN0331
Fox |  | Trustpower | Embedded | Hydro | Hydro | HKK0661
Kaniere Forks | Kaniere River | Trustpower | Embedded | Hydro | Hydro | HKK0661
McKays Creek | Kaniere River | Trustpower | Embedded | Hydro | Hydro | HKK0661
Wahapo (Okarito Forks) |  | Trustpower | Partially Embedded | Hydro | Hydro | HKK0661
Huntly |  | Genesis Energy | Grid Connected | Thermal | Coal_NI | HLY2201 | HLY2201 HLY1
Huntly |  | Genesis Energy | Grid Connected | Thermal | Coal_NI | HLY2202 | HLY2201 HLY4
Huntly e3p |  | Genesis Energy | Grid Connected | Thermal | Gas | HLY2202 | HLY2201 HLY5
Huntly p40 |  | Genesis Energy | Grid Connected | Thermal | Gas | HLY2202
Darfield |  | WD Boyes & Sons | Embedded | Thermal | Diesel | HOR0331
Mangapehi |  | Clearwater Hydro | Embedded | Hydro | Hydro | HTI0331
Marokopa Power Station |  | Marakopa Generation | Embedded | Hydro | Hydro | HTI0331
Piriaka |  | King Country Energy | Embedded | Hydro | Hydro | HTI0331
Mangahewa | Todd Energy | Todd Energy | Embedded | Thermal | Gas | HUI0331
Motukawa |  | Trustpower | Embedded | Hydro | Hydro | HUI0331
Mokoia Road, Hawera |  | Swift Energy | Embedded | Thermal | Unknown | HWA0331
Patea |  | Trustpower | Grid Connected | Hydro | Hydro | HWA1101
Kiwi Dairy, Hawera (Whareroa) |  | Todd Energy | Grid Connected Cogen | Cogeneration | Gas | HWA1102 | HWA1102 WAA0
Patearoa | Paerau Gorge Power Scheme | Trustpower | Embedded | Hydro | Hydro | HWA1102
Deep Stream |  | Trustpower | Embedded | Hydro | Hydro | HWB0331
Port Chalmers |  | Port Otago | Embedded | Unknown | Unknown | HWB0331
Mahinerangi |  | Trustpower | Embedded | Wind | Wind | HWB0331
Ravensbourne |  | Ravensdown Fertiliser Co-op | Embedded | Cogeneration | Unknown | HWB0332
Kew Hospital |  | Kew Hospital | Embedded | Unknown | Unknown | INV0331
FoodStuffs Hickory Place |  | Foodstuffs (South Island) | Embedded | Unknown | Unknown | ISL0331
Hornby, Christchurch |  | Ravensdown Fertiliser Co-op | Embedded | Thermal | Unknown | ISL0331
Middleton |  | CWF Hamilton & Co | Embedded | Unknown | Unknown | ISL0331
Templeton |  | Department of Corrections | Embedded | Thermal | Unknown | ISL0331
Christchurch Airport (Harewood) |  | Christchurch Airport Authority | Embedded | Backup generation | Unknown | ISL0661
Kawerau - BOP |  | Bay of Plenty Energy | Partially Embedded | Geothermal | Geothermal | KAW0111
Kawerau - KA24 |  | Geothermal Developments | Embedded | Geothermal | Geothermal | KAW0111
Kawerau - CHH |  | Carter Holt Harvey | Embedded | Cogeneration | Wood_waste | KAW0111
Kawerau - TPP |  | Norske Skog Tasman | Grid Connected Cogen | Cogeneration | Gas | KAW0112
Kawerau Geothermal |  | Mighty River Power | Grid Connected | Geothermal | Geothermal | KAW1101 | KAW1101 KAG0
Kinleith |  | Genesis Energy | Grid Connected Cogen | Cogeneration | Wood_waste | KIN0112
Ngawha |  | Top Energy | Embedded | Geothermal | Geothermal | KOE0331
Kapuni |  | Bay of Plenty Energy | Grid Connected Cogen | Cogeneration | Gas | KPA1101
Karapiro | Waikato Hydro Scheme | Mighty River Power | Grid Connected | Hydro | Hydro | KPO1101
Hokitika Diesel |  | Trustpower | Embedded | Thermal | Diesel | KUM0661
Dillmans | Dillmans Hydro Power Scheme | Trustpower | Embedded | Hydro | Hydro | KUM0661
Kumara | Dillmans Hydro Power Scheme | Trustpower | Embedded | Hydro | Hydro | KUM0661
Duffers | Dillmans Hydro Power Scheme | Trustpower | Embedded | Hydro | Hydro | KUM0662
Turitea Hydro |  | Palmerston North City Council | Embedded | Hydro | Hydro | LTN0331
Totara Road |  | Palmerston North City Council | Embedded | Thermal | Unknown | LTN0331
Tararua Stage 1 | Tararua Wind Farm | Trustpower | Embedded | Wind | Wind | LTN0331
Manapouri |  | Meridian Energy | Grid Connected | Hydro | Hydro | MAN2201
Aniwhenua |  | Bay of Plenty Energy | Partially Embedded | Hydro | Hydro | MAT1101
Matahina |  | Trustpower | Grid Connected | Hydro | Hydro | MAT1101
Marsden B |  | Mighty River Power | Grid Connected | Thermal | Coal_NI | MDN1101
Hampton Downs Landfill |  | EnviroWaste | Embedded | Other | Biogas | MER0331
Mangahao |  | Todd Energy | Grid Connected | Hydro | Hydro | MHO0331
Watercare Mangere |  | Watercare Services | Embedded | Cogeneration | Biogas | MNG0331
Pacific Steel |  | Vector | Embedded | Backup generation | Unknown | MNG0331
Brooklyn Power Station |  | Lloyd Wensley | Embedded | Hydro | Hydro | MOT0111
Wairua Falls |  | Northpower | Embedded | Hydro | Hydro | MPE0331
Maungatapere |  | Trustpower | Embedded | Thermal | Unknown | MPE0331
Whangarei |  | Northland District Health Board | Embedded | Thermal | Unknown | MPE0331
Onekaka |  | Onekaka Energy | Embedded | Hydro | Hydro | MPI0661
Pupu Hydro |  | Pupu Hydro Society | Embedded | Hydro | Hydro | MPI0661
Kourarau |  | Genesis Energy | Partially Embedded | Hydro | Hydro | MST0331
Maraetai | Waikato Hydro Scheme | Mighty River Power | Grid Connected | Hydro | Hydro | MTI2201
Ballance Agri |  | Trustpower | Embedded | Cogeneration | Unknown | MTM0111
Drysdale |  | Drysale Hydro Company | Embedded | Hydro | Hydro | MTN0331
Nga Awa Purua |  | Mighty River Power | Grid Connected | Geothermal | Geothermal | NAP2201 | NAP2201 NAP0
Monowai |  | Pioneer Generation | Embedded | Hydro | Hydro | NMA0331
White Hill |  | Meridian Energy | Embedded | Wind | Wind | NMA0331
New Plymouth |  | Contact Energy | Grid Connected | Thermal | Gas | NPL1101
Falls Dam |  | Pioneer Generation | Embedded | Hydro | Hydro | NSY0331
Paerau | Paerau Gorge Power Scheme | Trustpower | Embedded | Hydro | Hydro | NSY0331
Enfield |  | Network Waitaki | Embedded | Unknown | Unknown | OAM0331
Chathams Wind |  | CBD Energy | Embedded | Wind | Wind | OFFGRID
Ohau A | Waitaki Hydro Scheme | Meridian Energy | Grid Connected | Hydro | Hydro | OHA2201
Ohau B | Waitaki Hydro Scheme | Meridian Energy | Grid Connected | Hydro | Hydro | OHB2201
Ohau C | Waitaki Hydro Scheme | Meridian Energy | Grid Connected | Hydro | Hydro | OHC2201
Ohakuri | Waikato Hydro Scheme | Mighty River Power | Grid Connected | Hydro | Hydro | OHK2201
Ohaaki |  | Contact Energy | Grid Connected | Geothermal | Geothermal | OKI2201 | OKI2201 OKI0
Raetihi |  | Trustpower | Embedded | Hydro | Hydro | OKN0111
Kuratau |  | King Country Energy | Embedded | Hydro | Hydro | ONG0331
Mokauiti |  | King Country Energy | Embedded | Hydro | Hydro | ONG0331
Wairere Falls |  | King Country Energy | Embedded | Hydro | Hydro | ONG0331
Opunake |  | Trustpower | Embedded | Hydro | Hydro | OPK0331
Kongahu |  | Buller Electricity | Embedded | Unknown | Unknown | ORO1101
Greenmount Landfill |  | EnviroWaste | Embedded | Other | Biogas | OTA0221
Otahuhu A |  | Contact Energy | Grid Connected | Thermal | Gas | OTA1101
Otahuhu B |  | Contact Energy | Grid Connected | Thermal | Gas | OTA2202
Otematata |  | Network Waitaki | Embedded | Unknown | Unknown | OTT0011
Belfast |  | Christchurch City Council | Embedded | Unknown | Unknown | PAP0111
St Albans, Christchurch |  | Christchurch City Council | Embedded | Unknown | Unknown | PAP0661
Auckland District Hospital |  | Auckland District Hospital Board | Embedded | Cogeneration | Gas | PEN0331
Ascot Ave |  | Manson Developments | Embedded | Unknown | Unknown | PEN0331
Mansons Developments |  | Mighty River Power | Embedded | Unknown | Unknown | PEN1101
Plimmerton |  | Right House | Embedded | Unknown | Unknown | PNI0331
Poihipi Rd |  | Contact Energy | Grid Connected | Geothermal | Geothermal | PPI2201 | PPI2201 PPI0
Ravensdown |  | Vector | Embedded | Cogeneration | Unknown | RDF0331
Forest Research |  | Todd Energy | Embedded | Thermal | Gas | ROT0111
Wheao and Flaxy Scheme |  | Trustpower | Grid Connected | Hydro | Hydro | ROT0111
Fletcher Forests |  | Trustpower | Embedded | Thermal | Wood_waste | ROT0111
Roxburgh | Clutha Hydro Scheme | Contact Energy | Grid Connected | Hydro | Hydro | ROX1101
Rangipo | Tongariro Power Development | Genesis Energy | Grid Connected | Hydro | Hydro | RPO2201
Whisper Tech |  | Whisper Tech | Embedded | Thermal | Unknown | SBK0331
Stratford Austral Pacific |  | Austral Pacific Energy | Embedded | Unknown | Unknown | SFD0331
Stratford Peaker |  | Contact Energy | Grid Connected | Thermal | Gas | SFD2201 | SFD2201 SFD22
TCC - Taranaki Combined Cycle |  | Contact Energy | Grid Connected | Thermal | Gas | SFD2201 | SFD2201 SPL0
Christchurch Wind Turbine |  | Orion | Embedded | Wind | Wind | SPN0331
Southbridge Wind |  | Energy3 | Embedded | Wind | Wind | SPN0331
Redvale Landfill |  | Waste Management | Embedded | Other | Biogas | SVL0331
Southdown |  | Mighty River Power | Grid Connected | Thermal | Gas | SWN2201
Whitford Landfill |  | Waste Management | Embedded | Other | Biogas | TAK0331
Watercare Clevedon |  | Watercare Services | Embedded | Thermal | Unknown | TAK0331
Kaimai 5 | Kaimai Hydro Power Scheme | Trustpower | Embedded | Hydro | Hydro | TGA0331
Lloyd Mandeno | Kaimai Hydro Power Scheme | Trustpower | Embedded | Hydro | Hydro | TGA0331
Lower Mangapapa | Kaimai Hydro Power Scheme | Trustpower | Embedded | Hydro | Hydro | TGA0331
Ruahihi | Kaimai Hydro Power Scheme | Trustpower | Embedded | Hydro | Hydro | TGA0331
Tekapo A | Waitaki Hydro Scheme | Genesis Energy | Grid Connected | Hydro | Hydro | TKA0111
Tekapo B | Waitaki Hydro Scheme | Genesis Energy | Grid Connected | Hydro | Hydro | TKB2201
Tokaanu | Tongariro Power Development | Genesis Energy | Grid Connected | Hydro | Hydro | TKU0331
PukePine |  | PukePine Sawmills | Embedded | Thermal | Diesel | TMI0331
Anchor Products |  | Trustpower | Embedded | Thermal | Unknown | TMU0111
Te Awamutu - Anchor Products |  | Genesis Energy | Grid Connected Cogen | Cogeneration | Gas | TMU1101
Kaitawa | Waikaremoana | Genesis Energy | Grid Connected | Hydro | Hydro | TUI1101
Piripaua | Waikaremoana | Genesis Energy | Grid Connected | Hydro | Hydro | TUI1101
Tuai | Waikaremoana | Genesis Energy | Grid Connected | Hydro | Hydro | TUI1101
Tararua Stage 3 | Tararua Wind Farm | Trustpower | Grid Connected | Wind | Wind | TWC2201
Te Rere Hau |  | New Zealand Wind Farms | Partially Embedded | Wind | Wind | TWC2201
Horotiu Landfill |  | Green Energy | Embedded | Other | Biogas | TWH0331
Te Rapa |  | Contact Energy | Partially Embedded | Cogeneration | Gas | TWH0331 | TWH0331 TRC1
Te Uku |  | WEL Networks / Meridian Energy | Embedded | Wind | Wind | TWH0331
Te Apiti |  | Meridian Energy | Grid Connected | Wind | Wind | WDV1101
Pan Pac |  | Pan Pac Forest Products | Embedded | Cogeneration | Wood_waste | WHI0111
Whirinaki |  | Contact Energy | Grid Connected | Thermal | Diesel | WHI2201
Mokai I,II & III |  | Tuaropaki Power Company | Grid Connected | Geothermal | Geothermal | WKM2201 | WKM2201 MOK0
Maraetai Embedded |  | Mighty River Power | Embedded | Hydro | Hydro | WKM2201
Whakamaru | Waikato Hydro Scheme | Mighty River Power | Grid Connected | Hydro | Hydro | WKM2201
Tirohia Landfill |  | H.G. Leach & Co. | Embedded | Other | Biogas | WKO0331
Waipapa | Waikato Hydro Scheme | Mighty River Power | Grid Connected | Hydro | Hydro | WPA2201
Waihi Station |  | Trustpower | Embedded | Hydro | Hydro | WRA0111
Wairoa |  | Eastland Networks | Embedded | Unknown | Unknown | WRA0111
Rotokawa |  | Mighty River Power | Embedded | Geothermal | Geothermal | WRK0331
Te Huka |  | Contact Energy | Embedded | Geothermal | Geothermal | WRK0331
Hinemaiaia A | Hinemaiaia Hydro Scheme | Trustpower | Embedded | Hydro | Hydro | WRK0331
Hinemaiaia B | Hinemaiaia Hydro Scheme | Trustpower | Embedded | Hydro | Hydro | WRK0331
Hinemaiaia C | Hinemaiaia Hydro Scheme | Trustpower | Embedded | Hydro | Hydro | WRK0331
Iwitahi |  | Radio New Zealand | Embedded | Unknown | Unknown | WRK0331
Wairakei |  | Contact Energy | Grid Connected | Geothermal | Geothermal | WRK2201 | WRK2201 WRK0
Waitaki | Waitaki Hydro Scheme | Meridian Energy | Grid Connected | Hydro | Hydro | WTK0111
Omarama |  | Waitaki Power | Embedded | Unknown | Unknown | WTK0331
West Wind |  | Meridian Energy | Grid Connected | Wind | Wind | WWD1102, WWD1103

## Connection Type Definitions
Connection Type | Connection Description
Embedded | Connected to the local lines network - output is consumed locally
Partially Embedded | Connected to the local lines network - some injection into the grid occurs at the GXP the generation is embedded behind (ie at times generation exceeds consumption behind the GXP)
Grid Connected | Connected directly to the transmission grid
Combination, Grid Connected/Embedded | Connects to both the local lines network and the transmission grid
Grid Connected Cogen | Cogeneration plant associated with a load connected directly to the grid
Unknown | The type of connection is not known